## Narrative1
AR No. #
Boiler Tune
Recommendation
Implement a boiler tuning program to maintain an optimum air-fuel ratio, improving combustion efficiency and lowering fuel use. Tuning your boiler(s) will reduce associated fuel consumption by 3.2%.
Assessment Recommendation Summary
| Energy | Energy | Cost | Implementation | Payback
| (MMBtu)* | (therm)* | Savings | Cost | (Years)
| 235.6194 | 2356.194 | 2534.2909 | 1000 | 0.39459
* 1 MMBtu = 1,000,000 Btu, 1 therm = 100,000 Btu
Background
Ideally, a boiler would use just enough combustion air to burn all of the fuel, with no excess air. Excess air carries heat up the stack and reduces boiler efficiency. However, all burners require some excess air to ensure complete combustion. We assume that you can operate your boiler with 4.0% excess oxygen (O2). Depending on the boiler and control strategy it could be possible to reduce excess oxygen below 4.0% for additional savings, although care must be taken to ensure combustibles (unburned fuel) and carbon monoxide (CO) concentrations do not rise to unacceptable levels.
Efficiency can also be improved by cleaning scale from the waterside heat transfer surfaces. Scale deposits occur when calcium, magnesium, and silica, form a layer of material on the boiler heat exchanger surfaces. By removing the scale, heat transfer will improve, lowering stack temperatures.
We measured combustion gas temperatures and composition at several firing rates in order to establish an accurate model for boiler operation. With the combustion gas analysis, we used the ASME indirect method to calculate combustion efficiency for your boiler(s) at each firing rate. We then used the operating hours that plant personnel provided to calculate annual fuel use for your boiler(s). We verified the information that we measured, obtained from plant personnel, or assumed through boiler records or logs to the extent possible. Finally, we compared the calculated boiler fuel use with your fuel bills to verify the model is consistent with your operation.

## Narrative2
Proposal
We recommend you have a boiler specialist tune your boiler to 4.0% exhaust O2 and clean your boiler water side heat exchanger surfaces to increase combustion efficiency . We suggest this be done immediately and then once every year after. We estimate a boiler tune will cost $500 per boiler. Annual savings after deducting the annual cost to tune your boiler will be $2,534, paying for the initial implementation cost of the first tuning in 0.4 years.
Source: http://www.flickr.com/photos/anguskirk/

## Calc1
Boiler Tune
| Energy Savings Summary | [5 empty] | Equations | Information For Narrative
|  | Total Current Energy Use | (CE) | 7269 | MMBtu | (Rf. 1) | Eq. 1) Annual Energy Savings (ES) | Percent Energy Use Reduction | 3.241%
|  | Total Proposed Energy Use | (PE) | 7033.3806 | MMBtu | (Rf. 1) |  | Energy (MMBtu) | 235.6194
|  | Energy Savings | (ES) | 235.6194 | MMBtu | (Eq. 1) |  | Energy (therms) | 2356.194
[7 empty] | Eq. 2) Cost Savings (CS) | Cost Savings | 2534.2909
| Implementation Cost Summary | [6 empty] | Implementation Cost | 1000
| Labor Costs | [6 empty] | Payback | 0.39459
|  | Number of Boilers to Tune | (B) | 2 |  |  | Eq. 3) Implementation Costs (IC)
|  | Labor Cost per Boiler | (L) | 500 |  | (N. 1) |  | User Information
The calculations in this sheet are based on the ASME PTC 4 Indirect Methods for computing boiler efficiency.
Economic Results
|  | Cost Savings | (CS) | 2534.2909 |  | (Eq. 2) | References
|  | Implementation Costs | (IC) | 1000 |  | (Eq. 3) | Rf. 1) Savings were calculated using the Boiler Worksheet found on the following pages. | The proposed efficiency is calculated using an iterative process. In order for this to work you must enable iterative calculations, In Excel hit the office button and select "Excel Options" then click on the "Formulas" tab and check the "Enable Iterative Calculation" box.
|  | Payback | (PB) | 0.39459 | years
Notes
N. 1) The boiler should be tuned immediately, and then once every year to maintain optimum efficiency.

## Calc2
Boiler Tune
Efficiency Summary
|  | Current |  |  |  | Proposed |  |  |  | Percent
|  | High | Medium | Low | Standby | High | Medium | Low | Standby | Savings
| Boiler 1 | 71.44% | 68.01% | 60.76% | 18.11% | 73.3% | 70.05% | 62.67% | 21.55% | 2.879%
| Boiler 2 | 78.34% | - | - | - | 81.1% | - | - | - | 3.406%
|  | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | -
| Total | [8 empty] | 3.241%
Energy Savings Summary
|  | Current |  |  |  | Proposed |  |  |  | Total
|  | High | Medium | Low | Standby | High | Medium | Low | Standby | Savings
| Units | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu) | (MMBtu)
| Boiler 1 | 1000 | 750 | 500 | 19 | 974.703 | 728.1702 | 484.8274 | 15.9662 | 65.3332
| Boiler 2 | 5000 | - | - | - | 4829.7138 | - | - | - | 170.2862
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
| Total | 7269 |  |  |  | 7033.3806 |  |  |  | 235.6194
Cost Savings Summary
|  | Current |  |  |  | Proposed |  |  |  | Total
|  | High | Medium | Low | Standby | High | Medium | Low | Standby | Savings
| Boiler 1 | 15000 | 11250 | 7500 | 285 | 14620.5452 | 10922.5528 | 7272.4116 | 239.4927 | 979.9976
| Boiler 2 | 75000 | - | - | - | 72445.7067 | - | - | - | 2554.2933
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
|  | - | - | - | - | - | - | - | - | 0
| Total | 109035 |  |  |  | 105500.7091 |  |  |  | 3534.2909

## Boiler1
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location |  |  | Boiler 1
| Control Type |  | On-Off |  | Operating Hours |  |  | 3100 | hours
| Standby Cycle Time |  | 5.0963 | minutes | Maximum Firing Rate |  |  | 1 | MMBtu/hr
| Purge Cycle Time |  | 30 | seconds | Minimum Firing Rate |  |  | 20%
Enviromental Data
| Inlet Air Temperature |  | 80 | oF | Inlet Water Temperature |  |  | 50 | oF
| Purge Air Temperature |  | 75% |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  | 0.01 | lbv/lb air | Elevation |  |  | 0 | feet
Steam System
| Pressure Range |  | 10 | psi | Steam System Volume |  |  | 5.9752 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  | 100 | psig | Current Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  | 100 | psig | Proposed Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Fuel Properties
| Fuel Type |  | Propane |  | Fuel Cost |  |  | 15 | /MMBtu
| Percent Carbon |  | 81.8% | C | Percent Sulfur |  |  | 0% | S
| Percent Hydrogen |  | 18.2% | H | Percent Nitrogen |  |  | 0% | N2
| Percent Oxygen |  | 0% | O2 | Percent Ash |  |  | 0%
| Moisture Content |  | 0% |  | Higher Heating Value |  |  | 21670 | btu/lbm
| Molecular Weight |  | 44 | g/mol | High/Medium Fire Proposed O2 |  |  | 4% | O2
| Low/Standby Fire Proposed O2 |  | 5% | O2
Boiler Cycling
| DPVh |  | 806.9159 |  | Run Cycle |  |  | 4.8415 | minutes
| Off Cycle |  | 5.0963 | minutes | Total Cycle |  |  | 0.25482 | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 75% | 50% | 19% | 100% | 75% | 50% | 19%
| Fuel Input (MMBtu/hr) | 1 | 0.75 | 0.5 | 0.19 | 0.9747 | 0.72817 | 0.48483 | 0.15966
| Operating Hours | 1000 | 1000 | 1000 | 100 | 1000 | 1000 | 1000 | 100
| Energy Use (MMBtu/yr) | 1000 | 750 | 500 | 19 | 974.703 | 728.1702 | 484.8274 | 15.9662
Stack Conditions
| O2 | 10% | 9% | 8% | 7% | 4% | 4% | 5% | 5%
| CO2 | 8.5% | 8% | 7.5% | 6% | 11.16% | 11.16% | 10.51% | 10.51%
| CO | 8 | 8 | 8 | 9 | 8 | 8 | 8 | 9
| Stack Temperature | 350 | 325 | 300 | 300 | 350 | 325 | 300 | 300
| Net Stack Temperature | 270 | 245 | 220 | 220 | 270 | 245 | 220 | 220
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | 0.76911 | 0.57683 | 0.38456 | 0.14613 | 0.74966 | 0.56004 | 0.37289 | 0.1228
| Air Flow Rate (lbm/min) | 15.923 | 11.5515 | 7.4589 | 2.7487 | 12.9457 | 9.6714 | 6.6186 | 2.1796
Efficiencies
| Dry Gas Losses | 7.134% | 6.851% | 6.535% | 8.091% | 5.466% | 4.96% | 4.722% | 4.722%
| Moisture Formation | 8.769% | 8.686% | 8.602% | 8.602% | 8.769% | 8.686% | 8.602% | 8.602%
| Moisture in Fuel | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Carbon Monoxide | 0.003609% | 0.003835% | 0.00409% | 0.005752% | 0.002748% | 0.002748% | 0.00292% | 0.003285%
| Losses Due to Ash | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Moisture in the Air | 1.116% | 1.07% | 1.026% | 0.9949% | 0.9311% | 0.9223% | 0.9388% | 0.9388%
| Combustion Efficiency | 82.98% | 83.39% | 83.83% | 82.31% | 84.83% | 85.43% | 85.73% | 85.73%
| Thermal Losses | 11.53% | 15.38% | 23.07% | 60.71% | 11.53% | 15.38% | 23.07% | 60.71%
| Cycling Losses | - | - | - | 3.49% | - | - | - | 3.477%
| Boiler Efficiency | 71.44% | 68.01% | 60.76% | 18.11% | 73.3% | 70.05% | 62.67% | 21.55%
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler2
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location |  |  | Boiler 2
| Control Type |  | Full Modulating |  | Operating Hours |  |  | 1000 | hours
| Standby Cycle Time |  | 0.9683 | minutes | Maximum Firing Rate |  |  | 5 | MMBtu/hr
| Purge Cycle Time |  | 30 | seconds | Minimum Firing Rate |  |  | 20%
Enviromental Data
| Inlet Air Temperature |  | 80 | oF | Inlet Water Temperature |  |  | 50 | oF
| Purge Air Temperature |  | 75% |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  | 0.01 | lbv/lb air | Elevation |  |  | 0 | feet
Steam System
| Pressure Range |  | 10 | psi | Steam System Volume |  |  | 29.8762 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  | 100 | psig | Current Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  | 100 | psig | Proposed Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Fuel Properties
| Fuel Type |  | Propane |  | Fuel Cost |  |  | 15 | /MMBtu
| Percent Carbon |  | 81.8% | C | Percent Sulfur |  |  | 0% | S
| Percent Hydrogen |  | 18.2% | H | Percent Nitrogen |  |  | 0% | N2
| Percent Oxygen |  | 0% | O2 | Percent Ash |  |  | 0%
| Moisture Content |  | 0% |  | Higher Heating Value |  |  | 21670 | btu/lbm
| Molecular Weight |  | 44 | g/mol | High/Medium Fire Proposed O2 |  |  | 4% | O2
| Low/Standby Fire Proposed O2 |  | 5% | O2
Boiler Cycling
| DPVh |  | 4034.5797 |  | Run Cycle |  |  | 0.48415 | minutes
| Off Cycle |  | 0.9683 | minutes | Total Cycle |  |  | 0.48415 | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | 5 | - | - | - | 4.8297 | - | - | -
| Operating Hours | 1000 | 0 | 0 | 0 | 1000 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | 5000 | - | - | - | 4829.7138 | - | - | -
Stack Conditions
| O2 | 10% | - | - | - | 4% | - | - | -
| CO2 | 7.5% | - | - | - | 11.16% | - | - | -
| CO | 5 | - | - | - | 5 | - | - | -
| Stack Temperature | 350 | - | - | - | 350 | - | - | -
| Net Stack Temperature | 270 | - | - | - | 270 | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | 3.8456 | - | - | - | 3.7146 | - | - | -
| Air Flow Rate (lbm/min) | 79.6152 | - | - | - | 64.1469 | - | - | -
Efficiencies
| Dry Gas Losses | 8.042% | - | - | - | 5.466% | - | - | -
| Moisture Formation | 8.769% | - | - | - | 8.769% | - | - | -
| Moisture in Fuel | 0% | - | - | - | 0% | - | - | -
| Carbon Monoxide | 0.002557% | - | - | - | 0.001718% | - | - | -
| Losses Due to Ash | 0% | - | - | - | 0% | - | - | -
| Moisture in the Air | 1.116% | - | - | - | 0.9311% | - | - | -
| Combustion Efficiency | 82.07% | - | - | - | 84.83% | - | - | -
| Thermal Losses | 3.731% | - | - | - | 3.731% | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | 78.34% | - | - | - | 81.1% | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler3
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  | 30 | seconds | Minimum Firing Rate |  |  | 20%
Enviromental Data
| Inlet Air Temperature |  | 80 | oF | Inlet Water Temperature |  |  | 50 | oF
| Purge Air Temperature |  | 75% |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  | 0.01 | lbv/lb air | Elevation |  |  | 0 | feet
Steam System
| Pressure Range |  | 10 | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  | 100 | psig | Current Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  | 100 | psig | Proposed Steam Temperature |  |  | 338 | oF
| Saturated Vapor Specific Volume |  | 3.89 | ft3/lb | Saturated Liquid Enthalpy |  |  | 309 | btu/lbm
| Evaporated Enthalpy |  | 880 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1189 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler4
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  |  | seconds | Minimum Firing Rate
Enviromental Data
| Inlet Air Temperature |  |  | oF | Inlet Water Temperature |  |  |  | oF
| Purge Air Temperature |  |  |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  |  | lbv/lb air | Elevation |  |  |  | feet
Steam System
| Pressure Range |  |  | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  |  | psig | Current Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  |  | psig | Proposed Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler5
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  |  | seconds | Minimum Firing Rate
Enviromental Data
| Inlet Air Temperature |  |  | oF | Inlet Water Temperature |  |  |  | oF
| Purge Air Temperature |  |  |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  |  | lbv/lb air | Elevation |  |  |  | feet
Steam System
| Pressure Range |  |  | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  |  | psig | Current Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  |  | psig | Proposed Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler6
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  |  | seconds | Minimum Firing Rate
Enviromental Data
| Inlet Air Temperature |  |  | oF | Inlet Water Temperature |  |  |  | oF
| Purge Air Temperature |  |  |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  |  | lbv/lb air | Elevation |  |  |  | feet
Steam System
| Pressure Range |  |  | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  |  | psig | Current Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  |  | psig | Proposed Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler7
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  |  | seconds | Minimum Firing Rate
Enviromental Data
| Inlet Air Temperature |  |  | oF | Inlet Water Temperature |  |  |  | oF
| Purge Air Temperature |  |  |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  |  | lbv/lb air | Elevation |  |  |  | feet
Steam System
| Pressure Range |  |  | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  |  | psig | Current Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  |  | psig | Proposed Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Boiler8
Boiler Tune
Boiler Information
| Manufacturer |  |  |  | Location
| Control Type |  |  |  | Operating Hours |  |  | 0 | hours
| Standby Cycle Time |  | #DIV/0! | minutes | Maximum Firing Rate |  |  |  | MMBtu/hr
| Purge Cycle Time |  |  | seconds | Minimum Firing Rate
Enviromental Data
| Inlet Air Temperature |  |  | oF | Inlet Water Temperature |  |  |  | oF
| Purge Air Temperature |  |  |  | Atmospheric Pressure |  |  | 14.6958 | psia
| Air Humidity Ratio |  |  | lbv/lb air | Elevation |  |  |  | feet
Steam System
| Pressure Range |  |  | psi | Steam System Volume |  |  | 0 | ft3
| Steam Gas Constant |  | 0.11033 | btu/(lbm-R)
Current Steam Properties
| Current Steam Pressure |  |  | psig | Current Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Proposed Steam Properties
| Proposed Steam Pressure |  |  | psig | Proposed Steam Temperature |  |  | 212 | oF
| Saturated Vapor Specific Volume |  | 26.8 | ft3/lb | Saturated Liquid Enthalpy |  |  | 180 | btu/lbm
| Evaporated Enthalpy |  | 970 | btu/lbm | Saturated Vapor Enthalpy |  |  | 1150 | btu/lbm
Fuel Properties
| Fuel Type |  |  |  | Fuel Cost |  |  |  | /MMBtu
| Percent Carbon |  | #N/A | C | Percent Sulfur |  |  | #N/A | S
| Percent Hydrogen |  | #N/A | H | Percent Nitrogen |  |  | #N/A | N2
| Percent Oxygen |  | #N/A | O2 | Percent Ash |  |  | #N/A
| Moisture Content |  | #N/A |  | Higher Heating Value |  |  | #N/A | btu/lbm
| Molecular Weight |  | #N/A | g/mol | High/Medium Fire Proposed O2 |  |  | #N/A | O2
| Low/Standby Fire Proposed O2 |  | #N/A | O2
Boiler Cycling
| DPVh |  | 0 |  | Run Cycle |  |  | #DIV/0! | minutes
| Off Cycle |  | #DIV/0! | minutes | Total Cycle |  |  | #DIV/0! | minutes
Boiler Tune
Boiler Efficiency
|  | Current |  |  |  | Proposed
|  | High | Medium | Low | Standby | High | Medium | Low | Standby
Energy Use
| Percent Capacity | 100% | 70% | 40% | 10% | 100% | 70% | 40% | 10%
| Fuel Input (MMBtu/hr) | - | - | - | - | - | - | - | -
| Operating Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use (MMBtu/yr) | - | - | - | - | - | - | - | -
Stack Conditions
| O2 | - | - | - | - | - | - | - | -
| CO2 | - | - | - | - | - | - | - | -
| CO | - | - | - | - | - | - | - | -
| Stack Temperature | - | - | - | - | - | - | - | -
| Net Stack Temperature | - | - | - | - | - | - | - | -
Mass Flow Rates
| Fuel Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
| Air Flow Rate (lbm/min) | - | - | - | - | - | - | - | -
Efficiencies
| Dry Gas Losses | - | - | - | - | - | - | - | -
| Moisture Formation | - | - | - | - | - | - | - | -
| Moisture in Fuel | - | - | - | - | - | - | - | -
| Carbon Monoxide | - | - | - | - | - | - | - | -
| Losses Due to Ash | - | - | - | - | - | - | - | -
| Moisture in the Air | - | - | - | - | - | - | - | -
| Combustion Efficiency | - | - | - | - | - | - | - | -
| Thermal Losses | - | - | - | - | - | - | - | -
| Cycling Losses | - | - | - | - | - | - | - | -
| Boiler Efficiency | - | - | - | - | - | - | - | -
Notes
We calculate combustion efficiencies from the combustion gas conditions we measured using the ASME indirect method. We then calculate boiler efficiencies including radiation, convection and cycling losses. For more detailed information regarding how efficiency losses are calculated, refer to the Boiler Appendix.

## Fuel Properties
Fuel Type | Wood
Fuel Properties Summary
| C | S | H | N2 | O2 | Ash | MC | HHV | Molecular | Proposed O2
[9 empty] | Weight | High | Low
Units | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (Btu/lb) |  | (%) | (%)
Coal | 94.65% | 0.034% | 5.27% | 0.03% | 0.064% | 0% | 0% | 14203 | 483.44 | 4.5% | 5.5%
Natural Gas | 71.01% | 0% | 23.66% | 3.824% | 1.15% | 0% | 0% | 21869 | 16.7 | 4% | 5%
Fuel Oil 2 | 86.03% | 2% | 12.42% | 0.1% | 0% | 0.1% | 0.5% | 18800 | 208 | 4% | 5%
Fuel Oil 6 | 87.4% | 1.399% | 9.985% | 0.918% | 0.28% | 0% | 0% | 18300 | 338 | 4% | 5%
Propane | 81.8% | 0% | 18.2% | 0% | 0% | 0% | 0% | 21670 | 44 | 4% | 5%
Bio-Diesel | 86.03% | 2% | 12.42% | 0.1% | 0% | 0.1% | 0.5% | 18800 | 208 | 4% | 5%
Wood | 52.3% | 0% | 6.3% | 0.1% | 40.5% | 0.8% | 33% | 8600 | 26 | 8% | 8.5%
Wood Species | Douglas Fir Wood |  |  |  | Actual Wood Moisture Content (Wet Basis) |  |  |  | 50%
Wood Properties Summary
| C | S | H | N2 | O2 | Ash | MC | HHV | Percent
Combustible
Units | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (Btu/lb) | (%)
Douglas Fir Wood | 52.3% | 0% | 6.3% | 0.1% | 40.5% | 0.8% | 33% | 8600
Douglas Fir Bark | 56.2% | 0% | 6.2% | 0.1% | 37.3% | 0.2% | 33% | 10000
Western Hemlock Wood | 50.4% | 0% | 5.8% | 0.1% | 41.4% | 2.2% | 44% | 8500
Western Hemlock Bark | 53% | 0% | 6.2% | 0.1% | 39.3% | 1.5% | 41% | 9400 | 1.399%
Lodgepole Pine | 52.9% | 0% | 6.3% | 0.1% | 39.7% | 1% | 36% | 8600 | 0.1752%
Lodgepole Pine Bark | 55% | 0% | 5.8% | 0.1% | 38.6% | 0.8% | 50% | 10000
Ponderosa Pine | 52.9% | 0% | 6.3% | 0.1% | 39.7% | 1% | 52% | 9100
Ponderosa Pine Bark | 53.1% | 0% | 5.9% | 0.2% | 37.9% | 2.9% | 23% | 9500 | 3.747%
Redwood | 53.5% | 0% | 5.9% | 0.1% | 40.3% | 0.2% | 55% | 9000
Redwood Bark | 51.9% | 0% | 5.1% | 0.1% | 42.4% | 0.5% | 12% | 8350
Western Red Cedar | 52.9% | 0% | 6.3% | 0.1% | 39.7% | 1% | 33% | 9000
Western Red Cedar Bark | 53.1% | 0% | 5.9% | 0.2% | 37.9% | 2.9% | 32% | 8850
Port Orford Cedar | 52.9% | 0% | 6.3% | 0.1% | 39.7% | 1% | 30% | 9000
Port Orford Cedar Bark | 53.1% | 0% | 5.9% | 0.2% | 37.9% | 2.9% | 25% | 9000
Red Alder | 50.8% | 0% | 6.4% | 0.4% | 41.8% | 0.6% | 50% | 8000 | 2.009%
Red Alder Bark | 51.2% | 0% | 6% | 0.4% | 37.9% | 4.5% | 45% | 8600 | 0.5084%
Oregon Ash | 50.8% | 0% | 6.4% | 0.4% | 41.8% | 0.6% | 32% | 8200
Oregon Ash Bark | 51.2% | 0% | 6% | 0.4% | 37.9% | 4.5% | 32% | 8200
Bigleaf Maple | 50.8% | 0% | 6.4% | 0.4% | 41.8% | 0.6% | 38% | 8250
Bigleaf Maple Bark | 51.2% | 0% | 6% | 0.4% | 37.9% | 4.5% | 38% | 8300
Oregon White Oak | 50.8% | 0% | 6.4% | 0.4% | 41.8% | 0.6% | 41% | 8110
Oregon White Oak Bark | 51.2% | 0% | 6% | 0.4% | 37.9% | 4.5% | 41% | 8110
Generic Softwood | 52.9% | 0% | 6.3% | 0.1% | 39.7% | 1% | 50% | 9000
Generic Softwood Bark | 53.1% | 0% | 5.9% | 0.2% | 37.9% | 2.9% | 40% | 9100
Generic Hardwood | 50.8% | 0% | 6.4% | 0.4% | 41.8% | 0.6% | 50% | 9000 | 1.08%
Generic Hardwood Bark | 51.2% | 0% | 6% | 0.4% | 37.9% | 4.5% | 40% | 9100
Generic Wood | 37.5% | 0% | 7.18% | 0.01% | 53.2% | 0% | 50% | 9450
Taken from: Research Bulletin 60, OSU Forest Research Lab, 9/87.

## Steam Properties
Properties of Steam | [5 empty] | Linear Interpolation Formulas
Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy |  |  | Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy
|  |  | Saturated Liquid | Evaporated | Saturated Vapor |  |  |  | Saturated Liquid | Evaporated | Saturated Vapor
(psig) | (oF) | (ft3/lb) | (Btu/lb) | (Btu/lb) | (Btu/lb) | (psig) | (oF) | (ft3/lb) | (Btu/lb) | (Btu/lb) | (Btu/lb)
25 (vacuum) | 134 | 142 | 102 | 1017 | 1119 | 0 | 212 | 26.8 | 180 | 970 | 1150
20 (vacuum) | 162 | 73.9 | 129 | 1001 | 1130
15 (vacuum) | 179 | 51.3 | 147 | 990 | 1137
10 (vacuum) | 192 | 39.4 | 160 | 982 | 1142
5 (vacuum) | 203 | 31.8 | 171 | 976 | 1147
0 | 212 | 26.8 | 180 | 970 | 1150
1 | 215 | 25.2 | 183 | 968 | 1151
2 | 219 | 23.5 | 187 | 966 | 1153
3 | 222 | 22.3 | 190 | 964 | 1154
4 | 224 | 21.4 | 192 | 962 | 1154
5 | 227 | 20.1 | 195 | 960 | 1155
6 | 230 | 19.4 | 198 | 959 | 1157
7 | 232 | 18.7 | 200 | 957 | 1157
8 | 233 | 18.4 | 201 | 956 | 1157
9 | 237 | 17.1 | 205 | 954 | 1159
10 | 239 | 16.5 | 207 | 953 | 1160
12 | 244 | 15.3 | 212 | 949 | 1161
14 | 248 | 14.3 | 216 | 947 | 1163
16 | 252 | 13.4 | 220 | 944 | 1164
18 | 256 | 12.6 | 224 | 941 | 1165
20 | 259 | 11.9 | 227 | 939 | 1166
22 | 262 | 11.3 | 230 | 937 | 1167
24 | 265 | 10.8 | 233 | 934 | 1167
26 | 268 | 10.3 | 236 | 933 | 1169
28 | 271 | 9.85 | 239 | 930 | 1169
30 | 274 | 9.46 | 243 | 929 | 1172
32 | 277 | 9.1 | 246 | 927 | 1173
34 | 279 | 8.75 | 248 | 925 | 1173
36 | 282 | 8.42 | 251 | 923 | 1174
38 | 284 | 8.08 | 253 | 922 | 1175
40 | 286 | 7.82 | 256 | 920 | 1176
42 | 289 | 7.57 | 258 | 918 | 1176
44 | 291 | 7.31 | 260 | 917 | 1177
46 | 293 | 7.14 | 262 | 915 | 1177
48 | 295 | 6.94 | 264 | 914 | 1178
50 | 298 | 6.68 | 267 | 912 | 1179
55 | 300 | 6.27 | 271 | 909 | 1180
60 | 307 | 5.84 | 277 | 906 | 1183
65 | 312 | 5.49 | 282 | 901 | 1183
70 | 316 | 5.18 | 286 | 898 | 1184
75 | 320 | 4.91 | 290 | 895 | 1185
80 | 324 | 4.67 | 294 | 891 | 1185
85 | 328 | 4.44 | 298 | 889 | 1187
90 | 331 | 4.24 | 302 | 886 | 1188
95 | 335 | 4.05 | 305 | 883 | 1188
100 | 338 | 3.89 | 309 | 880 | 1189
105 | 341 | 3.74 | 312 | 878 | 1190
110 | 344 | 3.59 | 316 | 875 | 1191
115 | 347 | 3.46 | 319 | 873 | 1192
120 | 350 | 3.34 | 322 | 871 | 1193
125 | 353 | 3.23 | 325 | 868 | 1193
130 | 356 | 3.12 | 328 | 866 | 1194
135 | 358 | 3.02 | 330 | 864 | 1194
140 | 361 | 2.92 | 333 | 861 | 1194
145 | 363 | 2.84 | 336 | 859 | 1195
150 | 366 | 2.74 | 339 | 857 | 1196
155 | 368 | 2.68 | 341 | 855 | 1196
160 | 371 | 2.6 | 344 | 853 | 1197
165 | 373 | 2.54 | 346 | 851 | 1197
170 | 375 | 2.47 | 348 | 849 | 1197
175 | 377 | 2.41 | 351 | 847 | 1198
180 | 380 | 2.31 | 353 | 845 | 1198
185 | 382 | 2.29 | 355 | 843 | 1198
190 | 384 | 2.24 | 358 | 841 | 1199
195 | 386 | 2.19 | 360 | 839 | 1199
200 | 388 | 2.14 | 362 | 837 | 1199
205 | 390 | 2.09 | 364 | 836 | 1200
210 | 392 | 2.05 | 366 | 834 | 1200
215 | 394 | 2 | 368 | 832 | 1200
220 | 396 | 1.96 | 370 | 830 | 1200
225 | 397 | 1.92 | 372 | 828 | 1200
230 | 399 | 1.89 | 374 | 827 | 1201
235 | 401 | 1.85 | 376 | 825 | 1201
240 | 403 | 1.81 | 378 | 823 | 1201
245 | 404 | 1.78 | 380 | 822 | 1202
250 | 406 | 1.75 | 382 | 820 | 1202
255 | 408 | 1.72 | 383 | 819 | 1202
260 | 409 | 1.69 | 385 | 817 | 1202
265 | 411 | 1.66 | 387 | 815 | 1202
270 | 413 | 1.63 | 389 | 814 | 1203
275 | 414 | 1.6 | 391 | 812 | 1203
280 | 416 | 1.57 | 392 | 811 | 1203
285 | 417 | 1.55 | 394 | 809 | 1203
290 | 418 | 1.53 | 395 | 808 | 1203
295 | 420 | 1.49 | 397 | 806 | 1203
300 | 421 | 1.47 | 398 | 805 | 1203
305 | 423 | 1.45 | 400 | 803 | 1203
310 | 425 | 1.43 | 402 | 802 | 1204
315 | 426 | 1.41 | 404 | 800 | 1204
320 | 427 | 1.38 | 405 | 799 | 1204
325 | 429 | 1.36 | 407 | 797 | 1204
330 | 430 | 1.34 | 408 | 796 | 1204
335 | 432 | 1.33 | 410 | 794 | 1204
340 | 433 | 1.31 | 411 | 793 | 1204
345 | 434 | 1.29 | 413 | 791 | 1204
350 | 435 | 1.28 | 414 | 790 | 1204
355 | 437 | 1.26 | 416 | 789 | 1205
360 | 438 | 1.24 | 417 | 788 | 1205
365 | 440 | 1.22 | 419 | 786 | 1205
370 | 441 | 1.2 | 420 | 785 | 1205
375 | 442 | 1.19 | 421 | 784 | 1205
380 | 443 | 1.18 | 422 | 783 | 1205
385 | 445 | 1.16 | 424 | 781 | 1205
390 | 446 | 1.14 | 425 | 780 | 1205
395 | 447 | 1.13 | 427 | 778 | 1205
400 | 448 | 1.12 | 428 | 777 | 1205
450 | 460 | 1 | 439 | 766 | 1205
500 | 470 | 0.89 | 453 | 751 | 1204
550 | 479 | 0.82 | 464 | 740 | 1204
600 | 489 | 0.74 | 475 | 728 | 1203
650 | 497 | 0.69 | 483 | 719 | 1202
700 | 505 | 0.64 | 491 | 710 | 1201
750 | 513 | 0.6 | 504 | 696 | 1200
800 | 520 | 0.56 | 512 | 686 | 1198
900 | 534 | 0.49 | 529 | 666 | 1195
1000 | 546 | 0.44 | 544 | 647 | 1191
1250 | 574 | 0.34 | 580 | 600 | 1180
1500 | 597 | 0.23 | 610 | 557 | 1167
1750 | 618 | 0.22 | 642 | 509 | 1151
2000 | 636 | 0.19 | 672 | 462 | 1134
2250 | 654 | 0.16 | 701 | 413 | 1114
2500 | 669 | 0.13 | 733 | 358 | 1091
2750 | 683 | 0.11 | 764 | 295 | 1059
3000 | 696 | 0.08 | 804 | 213 | 1017
3206.2 | 705.4 | - | - | - | -