## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# |  |  |  | None | Improve Pump Efficiency | Optimize pumping in the [LOCATION] by [ACTIONS]. The system pumping efficiency can be improved from the current average of 55% to a reasonable average of 75% thereby reducing pump operation costs by 27%. | Insert Name | Electrical Consumption | 13333.3333 | 666.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 |  | N | 4000
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes | [21 empty] | Mikhail Jones
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Improve Pump Efficiency
Improve Pump Efficiency Template style 2015
Recommendation
Optimize pumping in the [LOCATION] by [ACTIONS]. The system pumping efficiency can be improved from the current average of 55% to a reasonable average of 75% thereby reducing pump operation costs by 27%.
INPUT HERE!
|  |  |  | Annual Savings Summary | [7 empty] | Annual Savings Summary
|  |  |  | Source |  | Quantity | Units |  | Cost Savings |  |  | Source | Quantity | Units | Cost Savings
|  |  |  | Electrical Consumption |  | 13333.3333 | kWh (site) |  | 666.6667 |  |  | Electrical Consumption | 13333.3333 | kWh (site) | 666.6667
|  |  |  | 0 |  | 0 |  |  | 0 |  | <-- Hide
|  |  |  | 0 |  | 0 |  |  | 0 |  | <-- Hide
|  |  |  | 0 |  | 0 |  |  | 0 |  | <-- Hide
|  |  |  | Total |  | 45.5067 | MMBtu |  | 666.6667 |  |  | Total | 45.5067 | MMBtu | 666.6667
Report Data Export page pulls values from this table
Implementation Cost Summary
|  |  |  | Description |  |  | Cost |  | Payback (yrs)
|  |  |  | Before Incentives |  |  | 5000 |  | 7.5
|  |  |  | After Incentives |  |  | 4000 |  | 6
Facility Background
[WHAT PUMP/PUMPS ARE PRESENT IN THE SYSTEM, AND WHAT ARE THEY DOING] [WHAT ARE THE OPERATION HOURS OF THESE PUMPS] [WHAT IS THE EFFICIENCY OF THE PUMPS, HOW DID YOU GET THAT NUMBER]. [ANY ADDITIONAL FACTORS LIKE PUMP MOTOR AGE, PUMP TYPE].
Technology Background
In any pumping system, opportunities for reduced energy consumption are typically available by:
| • | Reducing the required hydraulic horsepower: Hydraulic horsepower is defined as the power required to move a volume of liquid at a specified pressure and flow rate. There are two ways the required hydraulic horsepower can be reduced.
|  | • | Reducing pump outlet pressure: This can be accomplished by minimizing distribution line pressure losses though proper sizing of mainline to match the flow rate. When expanding or replacing mainlines we recommend consulting a professional to analyze which sizes may be most cost effective. Pump outlet pressure can also be reduced by eliminating throttle valve control or by minimizing end of line pressure requirements.
|  | • | Reducing pump flow: Annual water consumption can be reduced by ensuring excess water is not delivered to any end points. Water consumption can also be reduced by sealing line leaks and eliminating controls that bypass flow from the source without being used.
| • | Increasing system efficiency: Efficiency is defined as the ratio of output to the input of any system. Pumping system efficiency can be improved by maximizing the output by following these measures.
|  | • | Change operating point: All pumps are designed to operate at one Best Efficiency Point (BEP) on its flow versus head performance curve. When system requirements move away from this point the efficiency of the pump deteriorates. This can be solved by either better matching the end use requirements to the pump or vice versa, by replacing the pump with one that matches that end use requirements. Pump maintenance costs also tend to increase at operating points away from the BEP.
|  | • | Overhaul pump: The impeller and casing can be worn down over time, particularly if the pump has taken in dirt or other foreign matter or if it runs in a cavitating condition. This will increase the gap between casing and impeller, reducing the pump efficiency. Testing pump efficiency every two to three years can help ensure that pumps perform properly and that no significant losses occur. Depending on required head and flow, pumps can feasibly reach efficiencies as high as 80%. Unfortunately they are able to get the job done at extremely low efficiencies (20% or lower) with little outward sign of inefficient operation.
|  | • | Overhaul motor: Using Premium Efficiency (PE) motors instead of standard efficiency motors can increase system efficiency. PE motors are between 2 and 10 percent more efficient than standard efficiency motors, and the savings commonly justify the greater initial cost. Significant savings can occur when given the option of replacing an older motor with a new PE motor rather than rewinding. If performing a rewind is necessary, ensure that the efficiency of the motor is maintained through the rewind process.
|  | • | Consider Variable Speed Drive: Most pumps run at full speed no matter the load on the system. This can be very inefficient, particularly when a wide range of flow rates and pressures are needed. A more energy efficient system uses a variable speed drive (VSD) to slow the motor speed to match the end use requirements.
Proposal
[WHAT, FROM THE TECHNOLOGY BACKGROUND, IS HAPPENING TO THIS PUMP]. To correct this low system efficiency, we recommend taking the following actions:
| • | [LIST ACTIONS TO FIX THE EFFICIENCY PROBLEM].
For our estimates we assume you will be able to achieve a conservative system efficiency of at least 75%. However; you may be able to achieve a higher efficiency depending on the pump condition and the action taken, this would result in a slightly larger savings. If the previously mentioned actions are taken, they will save kWh annually and result in an annual cost savings of $667 for a net payback of 7.5 years and an implementation cost of $5,000.
Notes
An added benefit of optimizing pump efficiency will be that pump maintenance requirements are statistically lower when pumps operate closer to their Best Efficiency Point (BEP). However, this additional benefit has not been evaluated in this recommendation.
| Based on |  |  |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Original Template |  |  |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
Insert Name

## Analysis
AR No. # - Analysis
Improve Pump Efficiency Template style 2015
Data Collected |  |  |  |  | Equations | <-- (Insert --> Object --> Math Type 6.0 Equation)
Pump Operating Data |  |  |  |  | Eq. 1) Proposed Energy Consumption (EP)
Current Energy Consumption | (EC) | 50000 | kWh/yr | (Rf. 1)
Current Pump Efficiency | (ηC) | 55% |  | (Rf. 2) |  | NOTE: Include the pump curve on the following page (A scan will do). If unavailable, move Rf. 4 to notes section.
Maximum Pump Efficiency | (ηmax) | 80% |  | (Rf. 3) | Eq. 2) Annual Energy Savings (ES)
Proposed Pump Efficiency | (ηP) | 75% |  | (Rf. 4)
Utility Data
Incremental Electricity Cost | (ICE) | 0.05 | /kWh | (Rf. 5) | Eq. 3) Cost Savings (S)
Pump Analysis
Proposed Energy Consumption | (EP) | 36666.6667 | kWh/yr | (Eq. 1) | Eq. 4) Implementation Cost (CI)
Annual Energy Savings | (ES) | 13333.3333 | kWh/yr | (Eq. 2)
Implementation Analysis |  |  |  |  | Eq. 5) Simple Payback Period (tPB)
Material Costs
[MATERIAL COSTS] | (CM) | 4000 |  | (N. 1)
Labor Costs
[INSTALLATION COSTS] | (CL) | 1000 |  | (N. 1) | References
Rf. 1) Developed in the Motor Analysis Tool (MAT).
Economic Results
Cost Savings | (S) | 666.6667 | /yr | (Eq. 3) | Rf. 2) Developed in the Pump Efficiency Analysis Tool (PEAT).
Implementation Cost | (CI) | 5000 |  | (Eq. 4)
Simple Payback Period | (tPB) | 7.5 | yrs | (Eq. 5) | Rf. 3) According to the Hydraulics Institute Standard ANSI/HI-1.3 summarized in PSAT.
Notes |  |  |  |  | Rf. 4) Based on pump performance curve.
N. 1) [PLACE WHERE YOU FOUND DATA IN THIS NOTE AND IN THE REFERENCES].
Rf. 5) Based on site Utility Analysis, available in the Site Data section.

## Incentives
3 - AR No. 1 - Incentives
Improve Pump Efficiency Template style 2015
Recommendation Details
Implementation Cost |  | 5000 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 666.6667 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 7.5 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary
Description | Incentive | After Incentive | Payback | Notes
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
| 1000 |  |  |  | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 1000 | 4000 | 6 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.