## Instructions
Fan Efficiency Analysis Tool (FEAT)
Recommendation template version 2013a
Overview
The Fan Efficiency Analysis Tool (FEAT) calculates fan hydraluic efficiency based on motor information and ducting pressure readings. This can help identify fans that are operating away from their best efficiency point or that have sustained damage.
Instructions
In order to properly use this tool, you will need to collect the following information:
• | Inlet dynamic pressure
The inlet dynamic pressure is measured in the duct before the air reaches the fan with the pitot tubes and the magnehelic gauges or digital monometer. The dynamic pressure is the pressure due to the flow of fluid, and this can be directly related to the velocity of the fluid in the duct or pipe.
• | Outlet dynamic pressure
This is the same as the inlet however this is measured after the fan. This provides the velocity of the fluid coming out of the fan
• | Static differential pressure
The static differential pressure is the difference between the static pressure between the inlet and outlet of the fan. The static pressure is the pressure in the duct or pipe when the fluid is not flowing. This can be measured by connecting the static pressure outlets of two pitot tubes placed before and after the fan to a magnehelic gauge or digital monometer. The read-out will be your differential static pressure.
• | General pressure information
Static pressure is also known as the stagnation pressure. In the figure 1 the flow is parallel to the tube. When the flow reaches the end of the tube at location P2, the flow is stagnated by the air that is already in the tube. This stagnation forces pressure to increase in the pitot tube. The pitot tube measures this stagnation pressure as well as the static pressure through two different portions of the whole tube. The static pressure is measured by the same concept as the stagnation pressure however the inlet is perpendicular to the flow of the fluid so the pressure due to flow is not measured. The difference in this stagnation pressure and the static pressure is the dynamic pressure. This can be seen in the following equations1:
Eq. 1
|  | where: |  | is the total pressure
is the fluid density
is the velocity of fluid
is the static pressure at any point.
Eq. 2
|  | • | At a stagnation point, the velocity of the fluid is zero. Therefore the stagnation pressure (which is the static pressure at a stagnation point) is equal to total pressure.1
|  | • | Thus rearranging equation 1 and plugging in PStagnation with PTotal the dynamic pressure can be solved for and/or measured from the pitot tube.
Figure 1: Pitot tube in a pipeline representation2
• | Inlet/outlet Duct inside Diameter:
This is the diameter of the duct measured in inches by a measuring tape. This is required to calculate velocity.
• | Barometric Pressure:
The barometric pressure can be found by looking up local weather information from www.wunderground.com
• | Absolute Temperature
This is the temperature of the air outside the ducting; it can be measured or based on local weather information from the source stated above. Be sure to the temperature that is inputed is in Rankin.
• | Input power to fan Drive Shaft:
Preferably this power is measured directly or indirectly by measuring motor current (amperage) or using a power quality analyzer to measure power (kW) directly. If a measurement is not obtainable, a reasonable estimate by using load factor assumptions is acceptable, but will reduce the accuracy of the analysis.
• | Air Density:
Air density is calculated based on the environmental data. This is then used to calculate the gas velocity.
• | Gas compressibility Factor:
This is found based on the static pressure differential using table 3.1 of the DOE EERE Fan System Assessment Training Manual, 3rd edition3. This is used to modify the ideal gas law to account for real gas behavior. 2
• | Inlet/Outlet Gas Velocity:
The gas velocity is the speed of the gas inside the duct. It is used to determine the volumetric flow rate, and is calculated from the inlet/outlet dynamic pressures.
• | Inlet/Outlet Cross Sectional Area:
This is calculated form the diameter of the duct, and is also used to find the inlet volumetric flow rate
• | Inlet/Outlet Volumetric Flow Rate:
The volumetric flow rate is calculated from the values previously explained. The volumetric flow rate is used to find the average volumetric flow rate which is used determine the power Average Volumetric Flow rate produced by the fan.
• | Power output of fan:
The power output of the fan is determined based on volumetric flow rate, differential static pressure, and compressibility factor. Power is work divided by time, and work is force times distance. Flow rate times pressure of the gas is then the amount of power being put into the gas by the fan.
• | Mechanical Efficiency of Fan:
The mechanical efficiency of the fan is the power output of the fan divided by the power input to the fan. It is the ratio of the power output to input. An acceptable efficiency for recommendation can be found using the FSAT software or by looking at the fan blade efficiency template.
References:
1 http://en.wikipedia.org/wiki/stagnation_pressure
2 http://www.engineeringtoolbox.com/pitot-tubes-d_612/html
3 reference 3 in the Fan EfficiencyAnalysis Tool
Fan Identification
Fan Description
Fan Location
Data Collected
Fan Pressure Data
Inlet Dynamic Pressure |  |  |  |  | (pvi) | in.-H2O | (N. 1)
Outlet Dynamic Pressure |  |  |  |  | (pvo) | in.-H2O | (N. 1)
Static Differential Pressure |  |  |  |  | (Δps) | in.-H2O | (N. 1)
Ducting Data
Inlet Duct Inside Diameter |  |  |  |  | (di) | inches | (N. 2)
Outlet Duct Inside Diameter |  |  |  |  | (do) | inches | (N. 2)
Environmental Data
Barometric Pressure |  |  |  |  | (pb) | in.-Hg | (Rf. 1)
Absolute Temperature |  |  |  |  | (Ta) | oR | (Rf. 1)
Input Power Data
Input Power to Fan Drive Shaft |  |  |  |  | (Wi) | bhp | (Rf. 2)
Fluid Properties
Gas Compressibility Factor |  |  |  |  | (Kp) |  | (Rf. 3)

## FEAT
Fan Efficiency Analysis Tool (FEAT)
Recommendation template version 2013a
Fan Identification |  |  |  |  | Equations
Fan Description |  |  |  |  | Eq. 1) Air Density (ρ)
Fan Location
Eq. 2) Gas Velocity (V(i,o))
Data Collected
Fan Pressure Data
Inlet Dynamic Pressure | (pvi) |  | in.-H2O | (N. 1) | Eq. 3) Duct Cross Sectional Area (A(i,o))
Outlet Dynamic Pressure | (pvo) |  | in.-H2O | (N. 1)
Static Differential Pressure | (Δps) |  | in.-H2O | (N. 1)
Ducting Data |  |  |  |  | Eq. 4) Volumetric Flow Rate (Q(i,o))
Inlet Duct Inside Diameter | (di) |  | inches | (N. 2)
Outlet Duct Inside Diameter | (do) |  | inches | (N. 2) | Eq. 5) Avg. Volumetric Flow Rate (Qavg)
Environmental Data
Barometric Pressure | (pb) |  | in.-Hg | (Rf. 1)
Absolute Temperature | (Ta) |  | oR | (Rf. 1) | Eq. 6) Power Output of Fan (Wo)
Input Power Data
Input Power to Fan Drive Shaft | (Wi) |  | bhp | (Rf. 2)
Eq. 7) Mechanical Efficiency of Fan (ηf)
Fluid Properties
Air Density | (ρ) | - | lb./ft.3 | (Eq. 1)
Gas Compressibility Factor | (Kp) | 0.98 |  | (Rf. 3)
References
Fan Specifications |  |  |  |  | Rf. 1) Environmental data is based on local weather station readings, collected from www.wunderground.com
Inlet
Inlet Gas Velocity | (Vi) | - | fpm | (Eq. 2)
Inlet Duct Cross Sectional Area | (Ai) | - | ft2 | (Eq. 3) | Rf. 2) Input power to fan drive shaft is calculated using the Motor Analysis Tool (MAT) on the previous page.
Inlet Volumetric Flow Rate | (Qi) | - | cfm | (Eq. 4)
Outlet
Outlet Gas Velocity | (Vo) | - | fpm | (Eq. 2) | Rf. 3) Gas compressibility factor is estimated based on the static pressure differential using Table 3.1 of the DOE EERE Fan System Assessment Training Manual, 3rd Edition.
Outlet Duct Cross Sectional Area | (Ao) | - | ft2 | (Eq. 3)
Outlet Volumetric Flow Rate | (Qo) | - | cfm | (Eq. 4)
Fan Performance
Average Volumetric Flow Rate | (Qavg) | - | cfm | (Eq. 5) | Notes
Power Output of Fan | (Wo) | - | hp | (Eq. 6) | N. 1) A digital manometer was used to collect various pressure measurements.
Mechanical Efficiency of Fan | (ηf) | - |  | (Eq. 7)
N. 2) A tape measure was used to determine the size of various fan components.