## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# |  |  |  | None | AR Name | Install a heat exchanger to recover heat on the discharge streams from the juice resin columns. This recovered energy can be used to preheat the incoming water used to clean the same columns, which will save 5.4% of boiler fuel usage. | Insert Name | Natural Gas | 5382 | 53820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22612.069 |  | N | 12612.069
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - AR Name
Heat Exchanger Template style 2015
Recommendation
Install a heat exchanger to recover heat on the discharge streams from the juice resin columns. This recovered energy can be used to preheat the incoming water used to clean the same columns, which will save 5.4% of boiler fuel usage.
Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings
|  | Natural Gas |  | 5382 | MMBtu |  | 53820
|  | Total |  | 5382 | MMBtu |  | 53820
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Before Incentives |  |  | 22612.069 |  | 0.42014
|  | After Incentives |  |  | 12612.069 |  | 0.23434
| Facility Background | [7 empty] | Facility Background
Primary Data Collection Requirements ∙fluid properties (e.g. water, sugar water, salt water, juice, etc.) ∙flow rates of "cold" and "hot" fluids: such as 70 gallons per minue or 350 pounds per hour… ∙all inlet and outlet fluid temperatures that can be measured ∙annual operating hours for the process ∙space available for installation, used when considering what type of exchanger to recommend.
The facility currently has six resin exchange columns. These are primarily used to remove unwanted compounds from the juice being produced, especially those associated with color. At any given time, two of these columns are being used, two are being cleaned/regenerated, and two are on standby. The flow rates through these columns is variable (30 - 150 gallons per minute). However, we were informed that the flow rate averages around 70 GPM and is always flowing during light juice processing: four to five months a year during operating hours. The water used for cleaning can be pure, slightly acidic, or slightly caustic depending on the cleaning required. Prior to cleaning, the water is heated either directly or indirectly by the boiler. The temperature of the water being discharged from the columns after cleaning was measured at 153 °F while inlet water temperature from the city was right around 50 °F.
Technology Background
Technology Background
| A heat exchanger installed on site would allow for the heat contained in the discharged cleaning water to be recovered. The hot fluid in the heat exchanger delivers heat to the cold fluid, flowing the opposite direction. The counter-current configuration allows for maximum heat transfer and simultaneously cools the hot fluid and heats the cold fluid. The heat could be used for any desired purpose at the facility. This would reduce the steam demand on the natural gas fired boiler and would also avoid any inefficiencies associated with the combustion process, effectively reducing natural gas costs. | [7 empty] | The text in red should be changed to reflect the recommendation SPECIFICLY.
Some of the most common heat exchange equipment is briefly discussed below.
Double-Pipe and Multiple Double-Pipe In its simplest form, the double-pipe heat exchanger is simply a "tube inside of a tube". Modern industrial designs incorporate U-turns or hairpin turns inside the exchanger, where the flow in each section is essentially countercurrent. Double-pipe exchangers using traditional piping have limited applications but are useful where heat transfer magnitudes are small or where high pressures exist for both fluid streams.
Shell-and-Tube There are many different possible design configurations for shell-and-tube heat exchangers. There is even a dedicated nomenclature that describes the specifics of the design, which has been put forth by TEMA (Tubular Exchanger Manufacturer's Association). Consult their documentation for more details regarding specific naming standards. The fixed-tube type is the most commonly used, with a simple and economic construction. The U-tube type exchanger is able to handle stresses due to thermal expansion, but the U shaped design makes cleaning more difficult. The U-tube design is similar in cost and performance to the fixed-tube type when operating at low pressures, but has significant performance increases when operating at high pressures. The only other major disadvantage with the U-tube design is that complete counterflow across the tubes is not achieved except with certain designs. The floating-head type of exchanger, where one end of the tube bundle is not attached to the shell and is free-floating, is a more robust design that is capable of handling the stresses associated with high temperatures and high pressures. Fabrication is more complex and takes longer than the simpler designs, and as a result the floating-head type exchangers are typically 25% more expensive for an equivalent heat transfer surface area.
Plate-and-Frame A gasketed plate or plate-and-frame exchanger consists of a stack or a series of corrugated metal plates that are pressed together and held together by a frame and sealed. This forms an arrangement of narrow, interconnected passages that the fluids flow through. The hot and cold fluids pass through these channels in an alternating fashion and heat transfer occurs through the thin metal plate separating the two fluids. Overall surface area can be increased simply by adding more plates. The plates can be sealed with a rubber or other compressible material through simple compression, but this design fundamentally limits operational temperature and pressure limits. To circumvent this, the plates can be welded together but at the cost of creating a permanent exchanger that is much more difficult to clean, maintain, and adjust.
Other Designs There are many other type of heat exchange equipment, which will be briefly summarized here. Scraped-Surface exchangers are used with highly-viscous, crystallizing, or heavily fouling materials, where a rotating blade periodically removes buildup from heat exchange surfaces. Spiral plate and tube heat exchangers are comprised of spiraled plates that form countercurrent flow passages, and are good for small scale, compact heat exchange requirements. Gas-to-gas exchangers are typically nothing more than arrangements of tubes or surfaces that maximize surface area to facilitate heat transfer for low density, low heat capacity fluids such as air and stack exhaust. Air-cooled exchangers are similar to the heat sinks found in computers and electronic devices, and consist of a finned surface with a fan forcing air flow across the fins. There are many heat exchanger types that are designed specifically for condensation and evaporation that are not discussed in detail here as the design of these processes is often more complicated than simple heat exchange without phase change.
Proposal
Install a counter-current heat exchanger on the discharge streams from the resin columns on the juice lines. This would allow for a significant portion of currently wasted heat energy to be recovered and used. We suggest using the recovered energy to preheat the water used to clean the resin columns. This set up would allow the resin columns to be partially self-sustaining, with the hot discharge water warming the incoming cleaning water. This recovered heat will reduce the energy consumption on the natural gas fired boilers by 5%, or 5,382 MMBtu per year. This results in an annual cost savings of $53,820 with an implementation cost of $22,612 for a payback of 0.4 years.
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Original Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
| Date last Modified |  | Insert Name

## Data Preparation
AR No. # - Data Preparation
Heat Exchanger Template style 2015
Heading 2 |  |  |  |  | Equations
Heading 3 |  |  |  |  | Eq. 1) Equation 1 (V)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 2
Heading 3
Heading 4 | Variables | Calc | Units | (N. 1)
Heading 4 | Variables | Calc | Units | (Eq. 1)
Heading 4 | Variables | Calc | Units | (Eq. 2)
Heading 3
Heading 4 | Variables | Calc | Units | (N. 2)
Heading 4 | Variables | Calc | Units | (N. 3)

## Analysis
AR No. # - Analysis
Heat Exchanger Template style 2015
Data Collected |  |  |  |  | Equations
Flow Configuration |  |  |  |  | Eq. 1) Hot Exit Temp (TH,o)
Counter-current
Flows
Condensate (Hot) Flow | (ṁH) | 30000 | lb/hr | (N. 1)
Auxillary Water (Cold) Flow | (ṁC) | 30000 | lb/hr | (N. 1) | Eq. 2) Log Mean Temp Difference (DTLM)
Temperatures |  |  |  |  | If Counter-current flow
Hot Fluid Inlet Temperature | (TH,i) | 168 | °F | (N. 1)
Cold Fluid Inlet Temperature | (TC,i) | 64 | °F | (N. 1)
Operating Conditions
Annual Operating Hours | (tOH) | 3120 | hrs/yr | (N. 1)
Boiler Data |  |  |  |  | If Co-current flow
Annual Boiler Fuel Use |  | 100000 | MMBtu | (Rf. 1)
Boiler Efficiency | (hB) | 80% |  | (N. 1)
Incremental Energy Data
Incremental Natural Gas Cost | (ICN) | 10 | /MMBtu | (Rf. 1)
Eq. 3) Heat Exchange (Q)
Assumptions
Constants
Specific Heat (Hot Fluid) | (CPH) | 1 | Btu/lb∙°F | (Rf. 2) | Eq. 4) Energy Savings (ES)
Specific Heat (Cold Fluid) | (CPC) | 1 | Btu/lb∙°F | (Rf. 2)
Heat Transfer
Overall Heat Transfer Coefficient | (U) | 150 | Btu/hr∙°F∙ft2 | (Rf. 3)
References
Energy Savings Summary |  |  |  |  | Rf. 1) Developed in the Site Data section
Temperatures
Cold Exit Temp | (TC,o) | 110 | °F | (N. 2) | Rf. 2) www.engineeringtoolbox.com/ specific-heat-fluids-d_151.html
Hot Exit Temp | (TH,o) | 122 | °F | (Eq. 1)
Log Mean Temp Difference | (DTLM) | 58 | °F | (Eq. 2)(N. 3) | Rf. 3) Peters, Timmerhaus. Plant Design and Economics for Chemical Engineers., 2001
Energy Savings
Heat Exchange Rate | (Q) | 1380000 | Btu/hr | (Eq. 3)
Energy Savings | (ES) | 5382 | MMBtu | (Eq. 4) | Notes
N. 1) Data collected on site during the visit.
N. 2) Chosen based on maximum acceptable incremental payback period.
N. 3) When the temperature differentials between the two fluids are equal, the arithmetic mean is used instead of the log mean temperature difference.
Implementation Costs Summary |  |  |  |  | Equations
Material Costs |  |  |  |  | Eq. 5) Surface Area (A)
Heat Exchanger Cost per Sq. Ft. | (CE) | 100 | /ft2 | (N. 5)
Heat Exchanger Surface Area | (A) | 158.6207 | ft2 | (Eq. 5)
Piping Costs | (CP) | 5000 |  | (Rf. 4) | Eq.6) Total Material Cost (CTM)
Total Material Cost | (CTM) | 20862.069 |  | (Eq. 6)
Labor Costs
Labor Rate | (CLR) | 35 | /hr | (Rf. 4) | Eq.7) Total Labor Cost (CTL)
Labor Hours | (tL) | 50 | hrs | (Rf. 4)
Total Labor Cost | (CTL) | 1750 |  | (Eq. 7)
Eq. 8) Cost Savings (CS)
Economic Results
Cost Savings | (CS) | 53820 | /yr | (Eq. 8)
Implementation Costs | (CI) | 22612.069 |  | (Eq. 9) | Eq. 9) Implementation Costs (CI)
Simple Payback | (tPB) | 0.42014 | yrs | (Eq. 10)
Notes |  |  |  |  | Eq. 10) Simple Payback (tPB)
N. 5) Heat exchanger cost based on conversations with local vendors.
References
Rf. 4) RSMean Building Construction Cost Data 2009

## Table
AR No. # - Analysis | [9 empty] | <-- 650 pixels wide!
Heat Exchanger Template style 2015
Heat Exchanger Summary
Cold Exit Temp. | Hot Exit Temp. | LMTD | Heat Exchange | Energy Savings | Surface Area | Cost Savings | Implementation Cost | Simple Payback | Increm. Payback |  | Enter the Exit Temp that you want, based on Incremental Payback.
(TC,o)(N. 2) | (TH,o)(Eq. 1) | (DTLM)(Eq. 2) | (Q)(Eq. 3) | (ES)(Eq. 4) | (A)(Eq. 5) | (CS)(Eq. 6) | (CI)(Eq. 7) | (tPB)(Eq. 8) |  |  | Ex: If the client wants payback under 2 years, look at which incremental payback is just under 2 years. In this case, it is 1.7 years, corresponding to an Exit Temp of 140°F
(°F) | (°F) | (°F) | Btu/hr | MMBtu/yr | ft2 | $ | $ | years | years
70 | 162 | 98 | 180000 | 702 | 12.2449 | 7020 | 7974.4898 | 1.136 | --
75 | 157 | 93 | 330000 | 1287 | 23.6559 | 12870 | 9115.5914 | 0.70828 | 0.19506 |  | Proposed Cold Exit Temp | 110 | °F | 122 | 58 | 1380000 | 5382 | 158.6207 | 53820 | 22612.069 | 0.42014 | 0.48653
80 | 152 | 88 | 480000 | 1872 | 36.3636 | 18720 | 10386.3636 | 0.55483 | 0.21723 |  | Proposed Cold Exit Temp Increment | 5 | °F
85 | 147 | 83 | 630000 | 2457 | 50.6024 | 24570 | 11810.241 | 0.48068 | 0.2434
90 | 142 | 78 | 780000 | 3042 | 66.6667 | 30420 | 13416.6667 | 0.44105 | 0.2746
95 | 137 | 73 | 930000 | 3627 | 84.9315 | 36270 | 15243.1507 | 0.42027 | 0.31222
100 | 132 | 68 | 1080000 | 4212 | 105.8824 | 42120 | 17338.2353 | 0.41164 | 0.35813
105 | 127 | 63 | 1230000 | 4797 | 130.1587 | 47970 | 19765.873 | 0.41205 | 0.41498
110 | 122 | 58 | 1380000 | 5382 | 158.6207 | 53820 | 22612.069 | 0.42014 | 0.48653
115 | 117 | 53 | 1530000 | 5967 | 192.4528 | 59670 | 25995.283 | 0.43565 | 0.57833
120 | 112 | 48 | 1680000 | 6552 | 233.3333 | 65520 | 30083.3333 | 0.45915 | 0.69881
125 | 107 | 43 | 1830000 | 7137 | 283.7209 | 71370 | 35122.093 | 0.49211 | 0.86133
130 | 102 | 38 | 1980000 | 7722 | 347.3684 | 77220 | 41486.8421 | 0.53726 | 1.088
<--- Hide rows That have number errors. This simply means that these conditions are not possible.

## Incentives
3 - AR No. 1 - Incentives
Heat Exchanger Template style 2015
Recommendation Details
Implementation Cost |  | 22612.069 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 53820 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 0.42014 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary
Description | Incentive | After Incentive | Payback | Notes
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
| 10000 |  |  |  | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 10000 | 12612.069 | 0.23434 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.

## Data Sheet
Peters, Timmerhaus. Plant Design and Economics for Chemical Engineers., 2001 | [5 empty] | Heat Exchanger Type Description | Types: Heat Exchanger
Approximate design values of overall heat-transfer coefficient |  |  | 1 W/m2·K = | 5.67826 Btu/hr·ft2·F |  | Double-Pipe and Multiple Double-Pipe | Types: Flow
Coolers | [5 empty] | In its simplest form, the double-pipe heat exchanger is simply a "tube inside of a tube". Modern industrial designs incorporate U-turns or hairpin turns inside the exchanger, where the flow in each section is essentially countercurrent. Double-pipe exchangers using traditional piping have limited applications but are useful where heat transfer magnitudes are small or where high pressures exist for both fluid streams. | Co-current
Hot Fluid | Cold Fluid | Lower Range U (W/m2K) | Lower Range U (W/m2K) | Mean Value U | · |  | Counter-current
Water | Water | 1250 | 2500 | 1875
Methanol | Water | 1250 | 2500 | 1875
Ammonia | Water | 1250 | 2500 | 1875 |  | Shell-and-Tube
Aqueous Solutions | Water | 1250 | 2500 | 1875 |  | There are many different possible design configurations for shell-and-tube heat exchangers. There is even a dedicated nomenclature that describes the specifics of the design, which has been put forth by TEMA (Tubular Exchanger Manufacturer's Association). Consult their documentation for more details regarding specific naming standards. The fixed-tube type is the most commonly used, with a simple and economic construction. The U-tube type exchanger is able to handle stresses due to thermal expansion, but the U shaped design makes cleaning more difficult. The U-tube design is similar in cost and performance to the fixed-tube type when operating at low pressures, but has significant performance increases when operating at high pressures. The only other major disadvantage with the U-tube design is that complete counterflow across the tubes is not achieved except with certain designs. The floating-head type of exchanger, where one end of the tube bundle is not attached to the shell and is free-floating, is a more robust design that is capable of handling the stresses associated with high temperatures and high pressures. Fabrication is more complex and takes longer than the simpler designs, and as a result the floating-head type exchangers are typically 25% more expensive for an equivalent heat transfer surface area.
Light Organics* | Water | 375 | 750 | 562.5
Medium Organics** | Water | 250 | 600 | 425
Heavy Organics*** | Water | 25 | 375 | 200
Gases | Water | 10 | 250 | 130
Water | Brine | 500 | 1000 | 750
Light Organics* | Brine | 200 | 500 | 350
Heaters
Steam | Water | 1000 | 3500 | 2250
Steam | Methanol | 1000 | 3500 | 2250
Steam | Ammonia | 1000 | 3500 | 2250
Steam | Aqueous solutions: |  |  |  |  | Plate-and-Frame
| m < 2*10^-3 Pa·s | 1000 | 3500 | 2250 |  | A gasketed plate or plate-and-frame exchanger consiests of a stack or a series of corrugated metal plates that are pressed together and held together by a frame and sealed. This forms an arrangement of narrow, interconnected passages that the fluids flow through. The hot and cold fluids pass through these channels in an alternating fashion and heat transfer occurs through the thin metal plate separating the two fluids. Overall surface area can be increased simply by adding more plates. The plates can be sealed with a rubber or other compressible material through simple compression, but this design fundamentally limits operational temperature and pressure limits. To circumvent this, the plates can be welded together but at the cost of creating a permanent exchanger that is much more difficult to clean, maintain, and adjust.
| m > 2*10^-3 Pa·s | 500 | 2500 | 1500
Steam | Light Organics* | 500 | 1000 | 750
Steam | Medium Organics** | 250 | 500 | 375
Steam | Heavy Organics*** | 30 | 300 | 165
Steam | Gases | 25 | 250 | 137.5
Utility Fluid (dowtherm) | Gases | 20 | 200 | 110
Utility Fluid (dowtherm) | Heavy Organics*** | 30 | 300 | 165 |  | Others
Exchangers (no phase change) | [5 empty] | There are many other type of heat exchange equipment, which will be briefly summarized here. Scraped-Surface exchangers are used with highly-viscous, crystallizing, or heavily fouling materials, where a rotating blade periodically removes buildup from heat exchange surfaces. Spiral plate and tube heat exchangers are comprised of spiraled plates that form countercurrent flow passages, and are good for small scale, compact heat exchange requirements. Gas-to-gas exchangers are typically nothing more than arrangements of tubes or surfaces that maximize surface area to faciliatate heat transfer for low density, low heat capacity fluids such as air and stack exhaust. Air-cooled exchangers are similar to the heat sinks found in computers and electronic devices, and consist of a finned surface with a fan forcing air flow across the fins. There are many heat exchanger types that are designed specifically for condensation and evaporation that are not discussed in detail here as the design of these processes is often more complicated than simple heat exchange without phase change.
Water | Water | 1400 | 2850 | 2125
Aqueous Solutions | Aqueous solutions: | 1400 | 2850 | 2125
Light Organics* | Light Organics* | 300 | 425 | 362.5
Medium Organics** | Medium Organics** | 100 | 300 | 200
Heavy Organics*** | Heavy Organics*** | 50 | 200 | 125
Medium Organics** | Heavy Organics*** | 150 | 300 | 225
Light Organics* | Heavy Organics*** | 50 | 200 | 125
*Hydrocarbons through C8, gasoline, light alcohols, ketones (m < 0.5*10^-3 Pa·s)
**Absorber oil, hot gas oil, kerosene, light crudes (0.5*10^-3 Pa·s < m < 2.5*10^-3 Pa·s)
***Lube oils, fuel oils, cold gas oil, heavy and reduced crudes (2.5*10^-3 Pa·s < m < 5*10^-2 Pa·s)
Preliminary Selection Criteria for Heat Exchanger Type
Exchanger Type | Max. Pressure OR Approx Range (MPa) | Tempearture Range (°C) | Normal Area Range (m2) | Fluid Limitations | Key Features
Double Pipe | 30 (shell), 140 (tube) | -100-600 | 0.25-20 | materials of construction | modular construction, small scale
Multiple Pipe | 30 (shell), 140 (tube) | -100-600 | 10-200 | materials of construction | modular construction, small scale
Shell and Tube | 30 | -200-600+ | 3-1000 | materials of construction | adaptable, many types
Gasketed Plate | 0.1-2.5 | -25-175 | 1-2500 | gasket material, avoid gases | modular construction, minimal $/area cost
Welded Plate | 3 | >400 | 1-2500 | gasket material, avoid fouling fluids | DP between fluids <3MPa
Spiral Plate | 2 | up to 300 | 10-200 | materials of construction | for viscous, corrosive fluids
Spiral Tube | 50 | 350 | 1-50 | materials of construction | adaptable, low maintenance
Gas to Gas | 0.11 | up to 250 | 6-100 (low temp), 1200-3000 (regenerators) | materials of construction | many types, some for corrosive gases
Air-Cooled | variable | variable | 6-20,000 | materials of construction | use for heat rejection, standardized design