## Narrative
AR No. #
Isolate Unused Ends
Recommendation
Isolate and install insulation around unused ends in the greenhouse to reduce heat loss by 85.8% while reducing associated energy usage by 20.5%.
Assessment Recommendation Summary
| Energy | Energy | Cost |  | Implementation | Payback
| (MMBtu)* | (therm)* | Savings |  | Cost | (Years)
| 2046.7 | 20467.3 | 20467 |  | 17438 | 0.9
* 1 MMBtu = 1,000,000 Btu, 1 therm = 100,000 Btu
Background
Un-insulated or poorly insulated walls are a significant source of energy loss in any greenhouse. Temperature differentials between the walls and surroundings act as a driving force for conductive heat transfer between these bodies. The rate of this conductive heat transfer is directly proportional to the magnitude of the temperature differential. This differential creates a steady energy stream exiting the greenhouse, requiring the boiler to consume more energy to replenish the lost heat. Currently there are unused ends in the greenhouse that are not being used for production. These ends are still being heated and causing an additional heat loss and load on the boiler. By isolating these ends with a wall of insulation, heat loss will be dramatically decreased thus saving energy and increasing available heat, improving the efficiency of the system.
Proposal
We recommend installing corrugated high density polyethylene insulation around unused greenhouse ends to reduce heat loss. This will result in a cost savings of $20,467 and a 20.5% reduction in energy use for the greenhouse. There is an implementation cost of $17,438, resulting in a payback of 0.9 years.
Source: http://www.flickr.com/photos/e3000/

## Calculation1
Isolate Unused Ends
| Data Collected | [5 empty] | Equations
| Dimensional Data | [5 empty] | Eq. 1) Roof R-Value (RR)
|  | Length of an End | (L) | 200 | ft | (N. 1)
|  | Width of an End | (W) | 50 | ft | (N. 1)
|  | Height of an End | (H) | 10 | ft | (N. 1)
|  | Roof Angle | (θ) | 35 | degrees | (N. 1) | Eq. 2) Exterior End Wall R-Value (REW)
|  | Number of Unused Ends | (N) | 2
Energy Consumption Data
|  | Annual Boiler Energy Consumption | (ECB) | 10000 | MMBtu | (N. 2)
| Incremental Energy Data | [5 empty] | Eq. 3) Proposed Interior Wall R-Value (RIW)
|  | Incremental Boiler Fuel Cost | (ICN) | 10 | /MMBtu | (N. 3)
Assumptions
| Efficiencies | [5 empty] | Eq. 4) Roof Surface Area (SR)
|  | Boiler Efficiency | (ηB) | 75 | % | (Rf. 1)
Environmental Conditions
|  | Heating Degree Days | (HD1) | 5000 | °F-dys/yr | (Rf. 2)
| Material Properties | [5 empty] | Eq. 5) Exterior End Wall Area (SEW)
|  | Fiber Reinforced Plastic R-Value | (RC) | 0.83 |  | (Rf. 3)
|  | Corrugated Polyethylene R-Value | (RP) | 2.3 |  | (Rf. 3)
|  | Internal Film Resistance R-Value | (RIV) | 0.68 |  | (N. 4) (Rf. 4)
|  | Internal Film Resistance R-Value | (RIS) | 0.62 |  | (N. 5) (Rf. 4) | Eq. 6) Proposed Interior Wall Area (SIW)
|  | External Film Resistance R-Value | (RE) | 0.31 |  | (N. 6) (Rf. 4)
Conversion Factors
|  | Energy Conversion Factor | (CF1) | 1000000 | Btu/MMBtu
|  | Time Conversion Factor | (CF2) | 24 | hrs/day
References
| R-Value Development | [5 empty] | Rf. 1) This is the boiler efficiency that we collected during our visit. However, we recommended that you have your boiler tuned, which would increase the efficiency. If this action is taken, it will result in a slightly lower cost savings for this recommendation.
|  | Roof R-Value | (RR) | 1.76 |  | (Eq. 1)
|  | Exterior End Wall R-Value | (REW) | 1.82 |  | (Eq. 2)
|  | Proposed Interior Wall R-Value | (RIW) | 3.66 |  | (Eq. 3)
Surface Area Development
|  | Roof Surface Area | (SR) | 12207.7459 | ft2 | (Eq. 4) | Rf. 2) www.degreedays.net
|  | Exterior End Wall Area | (SEW) | 937.6297 | ft2 | (Eq. 5) | Rf. 3) http://attra.ncat.org
|  | Proposed Interior Wall Area | (SIW) | 4500 | ft2 | (Eq. 6) | Rf. 4) ASHRAE Handbook of Fundamentals 1997

## Calculation2
Isolate Unused Ends
| Heat Loss Development | [5 empty] | Equations | Information For Narrative
|  | Roof Heat Transfer | (HR) | 6936.2193 |  | (Rf. 5)(Eq. 7) | Eq. 7) Roof Heat Transfer (HR) | Percent Heat Loss Reduction | 85.8
|  | Exterior Wall Heat Transfer | (HEW) | 515.1812 |  | (Rf. 5)(Eq. 8) |  | Percent Energy Use Reduction | 20.5
|  | Interior Wall Heat Transfer | (HIW) | 1229.5082 |  | (Rf. 5)(Eq. 9) |  | Energy (MMBtu) | 2046.7
|  | Effective Heating Degree Days | (HD2) | 708.1679 |  | (N. 7)(Eq. 10) | Eq. 8) Exterior Wall Heat Transfer (HEW) | Energy (therms) | 20467.3
[8 empty] | Cost Savings | 20467
| Energy Savings Summary | [6 empty] | Implementation Cost | 17438
|  | Current Heat Loss | (QLC) | 1788.3361 | MMBtu | (Eq. 11) | Eq. 9) Interior Wall Heat Transfer (HIW) | Payback | 0.9
|  | Proposed Heat Loss | (QLP) | 253.2885 | MMBtu | (Eq. 12)
|  | Energy Savings | (ES) | 2046.7302 | MMBtu | (Eq. 13)
Eq. 10) Effective Heating Degree Day (HD2)
Implementation Costs Summary
Material Costs
|  | Insulation Cost | (CI) | 1.8125 | /ft2 | (Rf. 5)
|  | Material Costs | (CM) | 16312.5 |  | (Eq. 14) | Eq. 11) Current Heat Loss (QLC)
Labor Costs
|  | Labor Rate | (LR) | 50 | /hr | (Rf. 5)
|  | Labor Hours | (LH) | 0.0025 | hr/ft2 | (Rf. 5)
|  | Labor Costs | (CL) | 1125 |  | (Eq. 15) | Eq. 12) Proposed Heat Loss (QLP)
Economic Results
|  | Cost Savings | (CS) | 20467.302 | /yr | (Eq. 16)
|  | Implementation Costs | (IC) | 17437.5 |  | (Eq. 17) | Eq. 13) Energy Savings (ES)
|  | Payback | (PB) | 0.85197 | yrs
| References | [5 empty] | Eq. 14) Material Costs (CM)
Rf. 5) RSMean Building Construction Cost Data 2009
| Notes | [5 empty] | Eq. 15) Labor Costs (LM)
N. 1) Lengths and angles were measured during the site assessment.
N. 2) Boiler fuel consumption according to utility bills. See Site Data section.
| N. 3) Incremental boiler fuel cost according to utility bills. See Site Data section. | [5 empty] | Eq. 16) Cost Savings (CS)
N. 4) For still air on a vertical surface with a horizontal direction of heat flow.
N. 5) For still air on a 45o sloping surface with a upward direction of heat flow.
| N. 6) For moving air with a average velocity of 1.8 mph. (Linear extrapolation of R-value data.) | [5 empty] | Eq. 17) Implementation Costs (IC)
N. 7) Effective heating degree days is the temperature differential between the isolated end and the greenhouse.