## Report Data Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental
# |  |  | Building and Grounds | None | Lighting | Install (type of lights) in the (where) (operated using occupancy sensors?). This will increase lighting efficiency (reduce operating hours?), reducing associated annual energy consumption by 20%. | 0 | Electrical Consumption | 10080 | 957.6 | Electrical Demand | 30.24 | 211.68 | Ancillary Material Cost | 0 | 33.7044 | Administrative Costs | 0 | 132.3333 | 7301 |  | N
Resource Streams
Source Name | Source Code | Units |  | Some Useful ARC Codes (Updated June 2013)
Electrical Consumption | EC | kWh (site) |  | 2.7111 | Reduce illumination to minimum necessary levels
Electrical Demand | ED | kW Months / yr |  | 2.7112 | Reduce exterior illumination to minimum safe level
Other Electrical Fees | EF | no units |  | 2.7121 | Utilize daylight whenever possible in lieu of artificial light
Natural Gas | E2 | MMBtu |  | 2.7122 | Disconnect ballasts
L.P.G. | E3 | MMBtu |  | 2.7123 | Keep lamps and reflectors clean
#1 Fuel Oil | E4 | MMBtu |  | 2.7124 | Make a practice of turning off lights when not needed
#2 Fuel Oil | E5 | MMBtu |  | 2.7131 | Add area lighting switches
#4 Fuel Oil | E6 | MMBtu |  | 2.7132 | Install timers on light switches in little used areas
#6 Fuel Oil | E7 | MMBtu |  | 2.7133 | Use separate switches on perimeter lighting which may be turned off when natural light is available
Coal | E8 | MMBtu |  | 2.7134 | Use photocell controls
Wood | E9 | MMBtu |  | 2.7135 | Install occupancy sensors
Paper | E10 | MMBtu |  | 2.7141 | Lower light fixtures in high ceiling areas
Other Gas | E11 | MMBtu |  | 2.7142 | Utilize higher efficiency lamps and/or ballasts
Other Energy | E12 | MMBtu |  | 2.7143 | Use more efficient light source
Water Disposal | W1 | Gallons |  | 2.7144 | Install spectral reflectors / delamp
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Lighting
Lighting Analysis Template Apr. 2014a, style 2013b
Recommendation
Install (type of lights) in the (where) (operated using occupancy sensors?). This will increase lighting efficiency (reduce operating hours?), reducing associated annual energy consumption by 20%.
|  | Annual Savings Summary | [7 empty] | Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings |  |  | Source | Quantity | Units | Cost Savings
|  | Electrical Consumption |  | 10080 | kWh (site) |  | 957.6 |  |  | Electrical Consumption | 10080 | kWh (site) | 957.6
|  | Electrical Demand |  | 30.24 | kW Months / yr |  | 211.68 |  |  | Electrical Demand | 30.24 | kW Months / yr | 211.68
|  | Maintenance Material Cost |  |  |  |  | 33.7044 |  |  | Ancillary Material Cost |  | no units | 33.7044
|  | Maintenance Labor Cost |  |  |  |  | 132.3333 |  |  | Administrative Costs |  | no units | 132.3333
|  | Total |  | 34.403 | MMBtu |  | 1335.3178 |  |  | Total |  | MMBtu | 1335.3178
Report Data Export page pulls values from this table
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Implementation Cost |  |  | 7301 |  | 5.4676
Facility Background
The facility currently uses (stuff here). During the site assessment, plant personnel informed us that (stuff here). They also informed us that (stuff here). Motor information was collected for each system and is summarized in the following Motor Data Collection pages. (Something like this to provide facility specific information, keep all facility specific information here and general system information that applies to all facilities below.)
Technology Background
Use our stock technology descriptions here that describe how the system works and how energy would be saved.
Proposal
Install (type of lights, where, etc.). (Reasons why). (More on how it will be implemented). This will (increase lighting efficiency, reduce operating hours?), reducing annual energy cost by $958 and annual demand cost by $212. Additionally, improved lighting is estimated to reduce total maintenance costs by $166 per year. Annual cost savings are estimated at $1,335 after an implementation cost of $7,301, resulting in a payback period of 5.5 years.
A detailed listing of proposed lighting can be found on the summary pages in this recommendation.
| Notes | [7 empty] | <- Hide if there are no notes.
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Original Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
Insert Name

## Calculation
AR No. # - Analysis
Lighting Analysis Template Apr. 2014a, style 2013b
Data Collected |  |  |  |  | Equations
Energy Consumption Data |  |  |  |  | Eq. 1) Cost Savings (S)
Annual Energy Consumption | (E) | 50000 | kWh/yr | (Rf. 1)
[5 empty] | Eq. 2) Simple Payback (tPB) | <- HIDE A6-F6 IF NOT A REFRIGERATED SPACE
Savings Summary
Annual Energy Savings | (ES) | 10080 | kWh | (Rf. 2)
Annual Energy Cost Savings | (CSE) | 957.6 | /yr | (Rf. 2) | References
Annual Demand Savings | (DS) | 30.24 | kW-mo | (Rf. 2) | Rf. 1) Developed in the Lighting Inventory in the Site Data section.
Annual Demand Cost Savings | (CSD) | 211.68 | /yr | (Rf. 2)
Annual Material Cost Savings | (CSM) | 33.7044 | /yr | (Rf. 2, Rf. 4) | Rf. 2) Totals from the summary tables on the following pages.
Annual Labor Cost Savings | (CSL) | 132.3333 | /yr | (Rf. 2)
Rf. 3) Labor rates and replacement times associated with implementation cost were estimated using RSMeans 2012 Building Construction Cost Data.
Implementation Cost Summary
Maintenance Labor Rate | (CML) | 30 | /hr | (Rf. 3)
Electrician Labor Rate | (CEL) | 85 | /hr | (Rf. 3)
Controls Installation Time | (tCI) | 1 | hours | (Rf. 3) | Rf. 4) Lighting material costs used in this recommendation were found at: www.grainger.com/Grainger/lighting/ecatalog/
Fixture Replacement Time | (tFR) | 1 | hours | (Rf. 3)
Ballast Replacement Time | (tBR) | 0.5 | hours | (Rf. 3)
Lamp Replacement Time | (tLR) | 0.16667 | hours | (Rf. 3)
Economic Results
Cost Savings | (S) | 1335.3178 | /yr. | (Eq. 1)
Implementation Costs | (CI) | 7301 |  | (Rf. 2)
Payback | (tPB) | 5.4676 | years | (Eq. 2)
Notes | [5 empty] | <- Hide this line if there are no notes
Install (type of lights, where, etc.). (Reasons why). (More on how it will be implemented). This will (increase lighting efficiency, reduce operating hours?), reducing annual energy cost by $ and annual demand cost by $. Additionally, improved lighting is estimated to reduce total maintenance costs by $ per year. Annual cost savings are estimated at $ after an implementation cost of $, resulting in a payback period of 0.0 years.

## Summary
AR No. # - Summary | [8 empty] | AR No. # - Summary
Lighting Analysis Template Apr. 2014a, style 2013b | [8 empty] | Lighting Analysis Template Apr. 2014a, style 2013b | [6 empty] | Consider combining these tables into one page if they are small enough!
Savings Summary | [8 empty] | Implementation Cost Summary
# | Area Description | Energy Savings |  | Demand Savings |  | Material Savings | Labor Savings | Total Savings | # | Area Description | Recommendation | Material Cost | Installation Cost | Total Cost | Simple Payback
|  | (kWh/yr) | (/yr) | (kW-mo) | (/yr) | (/yr) | (/yr) | (/yr) |  |  |  | (/yr) | ($) | ($) | (years)
1 | Warehouse | 10080 | 957.6 | 30.24 | 211.68 | 33.7044 | 132.3333 | 1335.3178 | 1 | Warehouse | Replace lights | 5201 | 2100 | 7301 | 5.4676
2 | [8 empty] | 2 | [6 empty] | <-- Hide This Row
3 | [8 empty] | 3 | [6 empty] | <-- Hide This Row
4 | [8 empty] | 4 | [6 empty] | <-- Hide This Row
5 | [8 empty] | 5 | [6 empty] | <-- Hide This Row
6 | [8 empty] | 6 | [6 empty] | <-- Hide This Row
7 | [8 empty] | 7 | [6 empty] | <-- Hide This Row
8 | [8 empty] | 8 | [6 empty] | <-- Hide This Row
9 | [8 empty] | 9 | [6 empty] | <-- Hide This Row
10 | [8 empty] | 10 | [6 empty] | <-- Hide This Row
11 | [8 empty] | 11 | [6 empty] | <-- Hide This Row
12 | [8 empty] | 12 | [6 empty] | <-- Hide This Row
13 | [8 empty] | 13 | [6 empty] | <-- Hide This Row
14 | [8 empty] | 14 | [6 empty] | <-- Hide This Row
15 | [8 empty] | 15 | [6 empty] | <-- Hide This Row
16 | [8 empty] | 16 | [6 empty] | <-- Hide This Row
17 | [8 empty] | 17 | [6 empty] | <-- Hide This Row
18 | [8 empty] | 18 | [6 empty] | <-- Hide This Row
19 | [8 empty] | 19 | [6 empty] | <-- Hide This Row
20 | [8 empty] | 20 | [6 empty] | <-- Hide This Row
21 | [8 empty] | 21 | [6 empty] | <-- Hide This Row
22 | [8 empty] | 22 | [6 empty] | <-- Hide This Row
23 | [8 empty] | 23 | [6 empty] | <-- Hide This Row
24 | [8 empty] | 24 | [6 empty] | <-- Hide This Row
25 | [8 empty] | 25 | [6 empty] | <-- Hide This Row
26 | [8 empty] | 26 | [6 empty] | <-- Hide This Row
27 | [8 empty] | 27 | [6 empty] | <-- Hide This Row
28 | [8 empty] | 28 | [6 empty] | <-- Hide This Row
29 | [8 empty] | 29 | [6 empty] | <-- Hide This Row
30 | [8 empty] | 30 | [6 empty] | <-- Hide This Row
Totals |  | 10080 | 957.6 | 30.24 | 211.68 | 33.7044 | 132.3333 | 1335.3178 | Totals |  |  | 5201 | 2100 | 7301 | 5.4676

## (1)
AR No. # - Lighting Analysis
Lighting Analysis Template Apr. 2014a, style 2013b
General Data
Recommendation Description |  | Replace lights
Area Description |  | Warehouse
Recommended Foot-Candles |  | 50 | FC
Incremental Energy Cost | (CIE) | 0.095 | /kWh
Incremental Demand Cost | (CID) | 7 | /kW-mo
Incremental Implementation |  | No
Description |  | Existing | Proposed | Savings | Units
Fixtures
Fixture Code | GP-T12-8FT-4L-75W |  | MS-T5HO-4FT-4L-51W
Description |  | 8 ft. General Purpose T12HO | Motion Sensor T5HO
Quantity | (nF) | 20 | 20
Annual Operating Hours | (tOp) | 4000 | 4000 | 0 | hours
Output Factor | (OF) | 0.9 | 1 | -0.1
Luminous Efficiency | (ηl) | 0.75 | 0.8 | -0.05
Lamps
Lamps per Fixture | (nFL) | 4 | 4
Quantity | (nTL)(Eq. 1) | 80 | 80
Life | (tLL) | 12000 | 36000 | 24000 | hours
Lamp Cost | (CL) | 1.33 | 0.95 | 0.38
Watts per Lamp | (WL) | 75 | 51 | 24 | watts
Lumens | (l) | 6110 | 4700 | 1410 | Lm
Replacement Fraction | (RFL)(Eq. 2) | 0.33333 | 0.11111 | 0.22222
Annual Lamp Replacement Cost | (CLR)(Eq. 3) | 35.4667 | 8.4444 | 27.0222
Annual Maintenance Labor Cost | (CLM)(Eq. 4) | 133.3333 | 44.4444 | 88.8889
Ballast/Driver (Driver For LED Fixtures)
Ballasts per Fixture | (nFB) | 2 | 1 | 1
Quantity | (nTB)(Eq. 5) | 40 | 20 | 20
Life | (tBL) | 75000 | 72000 | 3000 | hours
Ballast Cost | (CB) | 64.2 | 117.25 | -53.05
Ballast Factor |  | 1 | 1
Input Watts | (WB) | 330 | 204 | 126 | watts
Replacement Fraction | (RFB)(Eq. 6) | 0.053333 | 0.055556 | -0.0022222
Annual Ballast Replacement Cost | (CBR)(Eq. 7) | 136.96 | 130.2778 | 6.6822
Annual Maintenance Labor Cost | (CBM)(Eq. 8) | 90.6667 | 47.2222 | 43.4444
Power and Energy
Lighting Power | (PL)(Eq. 9) | 6.6 | 4.08 | 2.52 | kW
Energy Use | (E)(Eq. 10) | 26400 | 16320 | 10080 | kWh
AR No. # - Lighting Analysis
Recommendation template version 2013b
Description |  | Existing | Proposed | Savings | Units
Light Level Check
Total Lumens | (lT)(Eq. 11) | 439.92 | 376 | 63.92 | kLm
Foot-Candles | (FC)(Eq. 12) | 50 | 45.584 | 4.416 | FC | <-- Check light levels! Try to find expected or propsed fc off of fixture specification sheets online or wherever you can find them.
Lighting Efficacy | (LE)(Eq. 13) | 66.6545 | 92.1569 | 25.5023 | Lm/W
Operating Costs
Demand Cost | (CD)(Eq. 14) | 554.4 | 342.72 | 211.68
Energy Cost | (CE)(Eq. 15) | 2508 | 1550.4 | 957.6
Maintenance Material Cost | (CMM)(Eq. 16) | 172.4267 | 138.7222 | 33.7044
Maintenance Labor Cost | (CML)(Eq. 17) | 224 | 91.6667 | 132.3333
Total Operating Cost | (CTOp)(Eq. 18) | 3458.8267 | 2123.5089 | 1335.3178
Recommendation Summary
Fixture Cost (with Ballast) | (CF) |  | 256.25 | /fixture
Sensor Cost | (CS) |  |  | /unit
Number of Sensors | (nS) |  |  | units
Materials Cost | (CM)(Eq. 19) |  | 5201 |  |  | <-- Add Formula in Formula sheet to match how Materials Cost is actually being calculated.
Labor Cost | (CLB)(Eq. 20) |  | 2100 |  |  | <-- Add Formula in Formula sheet to match how Labor Cost is actually being calculated.
Total Implementation Cost | (CI)(Eq. 21) |  | 7301
Cost Savings | (S)(Eq. 22) |  | 1335.3178 | /year
Simple Payback | (tPB)(Eq. 23) |  | 5.4676 | years
Picture
Notes
Pictures of Room
AND/OR
Room Highlighted on Facility Map

## Equation Sheet
AR No. # - Lighting Analysis
Lighting Analysis Template Apr. 2014a, style 2013b
Equations |  |  | <- MAKE SURE TO CHANGE EQUATIONS IF THERE ARE ANY SPECIAL CIRCUMSTANCES.
Lamps |  | Light Level Check
Eq. 1) Quantity (nTL) |  | Eq. 11) Total Lumens (lT)
Eq. 2) Replacement Fraction (RFL)
Eq. 12) Proposed Foot-candles (FC)
Eq. 3) Annual Replacement (CLR)
Eq. 4) Annual Maintenance Labor Cost (CLM) |  | Eq. 13) Lighting Efficiency (ƞL)
Ballasts
Eq. 5) Quantity (nTB) |  | Operating Costs | <-- Add Formula in Formula sheet to match how Materials Cost is actually being calculated.
|  | Eq. 14) Demand Cost (CD) | <-- Add Formula in Formula sheet to match how Labor Cost is actually being calculated.
Eq. 6) Replacement Fraction (RFB)
Eq. 15) Energy Cost (CE)
Eq. 7) Annual Replacement Cost (CBR) |  | Eq. 16) Maintenance Material Cost (CMM)
Eq. 8) Annual Maintenance Labor Cost (CBM) |  | Eq. 17) Maintenance Labor Cost (CML)
Eq. 18) Total Operating Cost (CTOp)
Power and Energy
Eq. 9) Lighting Power (PL)
Recommendation Summary
Eq. 19) Materials Cost (CM)
Eq. 10) Energy Use (E)
Eq. 20) Labor Cost (CL)
Eq. 21) Total Implementation Cost (CI)
Eq. 22) Cost Savings (S)
Eq. 23) Simple Payback (tPB)
Install (type of lights, where, etc.). (Reasons why). (More on how it will be implemented). This will (increase lighting efficiency, reduce operating hours?), reducing annual energy cost by $ and annual demand cost by $. Additionally, improved lighting is estimated to reduce total maintenance costs by $ per year. Annual cost savings are estimated at $ after an implementation cost of $, resulting in a payback period of 0.0 years.

## Fixture Data
Fixture Code | Description | Type | Lamp Size | Length (ft) | Lamps/ Fixture | Watts/ Lamp | Lumens Mean | Lamp Life | Input Watts (Total) | Input Watts (Per Ballast) | Ballast/ Fixture | Ballast Life | Ballast Factor | Fixture Cost (w/ Ballast) | Lamp Cost | Ballast Cost | Lighting Efficiency | Additonal Information
OF-T12-4FT-2L-34W | 4 ft. Office T12 | OF | T12 | 4 | 2 | 34 | 2610 | 20000 | 72 | 72 | 1 | 75000 | 1 | 80.9 | 0.4 | 31.45 | 9%
OF-T12-4FT-2L-40W | 4 ft. Office T12 | OF | T12 | 4 | 2 | 40 | 2910 | 20000 | 87 | 87 | 1 | 75000 | 1 | 80.9 | 0.87 | 31.45 | 9%
OF-T12-4FT-3L-34W | 4 ft. Office T12 | OF | T12 | 4 | 3 | 34 | 2610 | 20000 | 108 | 108 | 1 | 75000 | 1 | 79.2 | 0.4 | 37.45 | 9%
OF-T12-4FT-3L-40W | 4 ft. Office T12 | OF | T12 | 4 | 3 | 40 | 2910 | 20000 | 131 | 131 | 1 | 75000 | 1 | 79.2 | 0.87 | 37.45 | 9%
OF-T12-4FT-4L-34W | 4 ft. Office T12 | OF | T12 | 4 | 4 | 34 | 2610 | 20000 | 144 | 72 | 2 | 75000 | 1 | 78.05 | 0.4 | 31.45 | 9%
OF-T12-4FT-4L-40W | 4 ft. Office T12 | OF | T12 | 4 | 4 | 40 | 2910 | 20000 | 174 | 87 | 2 | 75000 | 1 | 78.05 | 0.87 | 31.45 | 9%
OF-T8-4FT-2L-32W | 4 ft. Office T8 | OF | T8 | 4 | 2 | 32 | 2660 | 36000 | 62 | 62 | 1 | 75000 | 0.96875 | 80.9 | 0.31 | 38.45 | 13.5%
OF-T8-4FT-3L-32W | 4 ft. Office T8 | OF | T8 | 4 | 3 | 32 | 2660 | 36000 | 93 | 93 | 1 | 75000 | 0.96875 | 79.2 | 0.31 | 42.65 | 13.5%
OF-T8-4FT-4L-32W | 4 ft. Office T8 | OF | T8 | 4 | 4 | 32 | 2660 | 36000 | 124 | 62 | 2 | 75000 | 0.96875 | 78.05 | 0.31 | 45.15 | 13.5%
OF-T5-4FT-2L-28W | 4 ft. Office T5 | OF | T5 | 4 | 2 | 28 | 2726 | 36000 | 58 | 58 | 1 | 75000 | 1 | 211.9 | 10.4 | 64.6 | 14%
HD-T12-4FT-2L-34W | 4 ft. Heavy Duty T12 | HD | T12 | 4 | 2 | 34 | 2610 | 20000 | 72 | 72 | 1 | 75000 | 1 | 92.95 | 0.4 | 31.45 | 9%
HD-T12-4FT-2L-40W | 4 ft. Heavy Duty T12 | HD | T12 | 4 | 2 | 40 | 2910 | 20000 | 87 | 87 | 1 | 75000 | 1 | 92.95 | 0.87 | 31.45 | 9%
HD-T12-8FT-2L-60W | 8 ft. Heavy Duty T12 | HD | T12 | 8 | 2 | 60 | 5060 | 12000 | 130 | 130 | 1 | 75000 | 1 | 155 | 1.33 | 64.2 | 9%
HD-T12-8FT-2L-75W | 8 ft. Heavy Duty T12 | HD | T12 | 8 | 2 | 75 | 6110 | 12000 | 165 | 165 | 1 | 75000 | 1 | 155 | 1.33 | 64.2 | 9%
HD-T12-8FT-2L-95W | 8 ft. Heavy Duty T12HO | HD | T12 | 8 | 2 | 95 | 7520 | 12000 | 203 | 203 | 1 | 75000 | 1 | 155 | 1.33 | 80.1 | 9%
HD-T12-8FT-2L-110W | 8 ft. Heavy Duty T12HO | HD | T12 | 8 | 2 | 110 | 8280 | 12000 | 237 | 237 | 1 | 75000 | 1 | 155 | 2 | 80.1 | 9%
HD-T12-8FT-2L-185W | 8 ft. Heavy Duty T12VHO | HD | T12 | 8 | 2 | 185 | 9380 | 9000 | 402 | 402 | 1 | 75000 | 1 | 188.75 | 2 | 103.8 | 9%
HD-T12-8FT-2L-215W | 8 ft. Heavy Duty T12VHO | HD | T12 | 8 | 2 | 215 | 10125 | 10000 | 467 | 467 | 1 | 75000 | 1 | 188.75 | 2.8 | 103.8 | 9%
HD-T12-8FT-2L-220W | 8 ft. Heavy Duty T12VHO | HD | T12 | 8 | 2 | 220 | 10600 | 10000 | 478 | 478 | 1 | 75000 | 1 | 188.75 | 3.67 | 103.8 | 9%
HD-T8-4FT-2L-32W | 4 ft. Heavy Duty T8 | HD | T8 | 4 | 2 | 32 | 2660 | 36000 | 62 | 62 | 1 | 75000 | 0.96875 | 92.95 | 0.31 | 38.45 | 13.5%
HD-T8-4FT-4L-32W | 4 ft. Heavy Duty T8 | HD | T8 | 4 | 4 | 32 | 2660 | 36000 | 112 | 112 | 1 | 75000 | 0.875 | 166.75 | 0.31 | 41.85 | 13.5%
HD-T8-8FT-2L-59W | 8 ft. Heavy Duty T8 | HD | T8 | 8 | 2 | 59 | 5500 | 20000 | 110 | 110 | 1 | 75000 | 0.9322 | 175 | 1.31 | 54.25 | 13.5%
HD-T8-8FT-2L-86W | 8 ft. Heavy Duty T8 | HD | T8 | 8 | 2 | 86 | 7600 | 18000 | 160 | 160 | 1 | 75000 | 0.93023 | 184.5 | 2.38 | 93.95 | 13.5%
GP-T12-4FT-2L-34W | 4 ft. General Purpose T12 | GP | T12 | 4 | 2 | 34 | 2650 | 20000 | 72 | 72 | 1 | 75000 | 1 | 58 | 0.4 | 31.45 | 9%
GP-T12-4FT-2L-40W | 4 ft. General Purpose T12 | GP | T12 | 4 | 2 | 40 | 2910 | 20000 | 87 | 87 | 1 | 75000 | 1 | 58 | 0.87 | 31.45 | 9%
GP-T12-8FT-2L-60W | 8 ft. General Purpose T12 | GP | T12 | 8 | 2 | 60 | 5060 | 12000 | 130 | 130 | 1 | 75000 | 1 | 90.3 | 1.33 | 64.2 | 9%
GP-T12-8FT-2L-75W | 8 ft. General Purpose T12 | GP | T12 | 8 | 2 | 75 | 6110 | 12000 | 165 | 165 | 1 | 75000 | 1 | 90.3 | 1.33 | 64.2 | 9%
GP-T12-8FT-2L-95W | 8 ft. General Purpose T12HO | GP | T12 | 8 | 2 | 95 | 7520 | 12000 | 203 | 203 | 1 | 75000 | 1 | 110.05 | 1.33 | 80.1 | 9%
GP-T12-8FT-2L-110W | 8 ft. General Purpose T12HO | GP | T12 | 8 | 2 | 110 | 8280 | 12000 | 237 | 237 | 1 | 75000 | 1 | 110.05 | 2 | 80.1 | 9%
GP-T12-8FT-4L-75W | 8 ft. General Purpose T12HO | GP | T12 | 8 | 4 | 75 | 6110 | 12000 | 330 | 165 | 2 | 75000 | 1 | 182.6 | 1.33 | 64.2 | 9%
GP-T8-4FT-1L-32W | 4 ft. General Purpose T8 | GP | T8 | 4 | 1 | 32 | 2660 | 36000 | 28 |  | 1 | 75000 | 0.875 | 56.35 | 0.31 | 32.8 | 13.5%
GP-T8-4FT-2L-32W | 4 ft. General Purpose T8 | GP | T8 | 4 | 2 | 32 | 2660 | 36000 | 62 | 62 | 1 | 75000 | 0.96875 | 58 | 0.31 | 32.8 | 13.5%
GP-T8-4FT-4L-32W | 4 ft. General Purpose T8 | GP | T8 | 4 | 4 | 32 | 2660 | 36000 | 112 | 112 | 1 | 75000 | 0.875 | 103.55 | 0.31 | 41.85 | 13.5%
GP-T8-8FT-2L-59W | 8 ft. General Purpose T8 | GP | T8 | 8 | 2 | 59 | 5500 | 20000 | 110 | 110 | 1 | 75000 | 0.9322 | 90.3 | 1.31 | 44.9 | 13.5%
GP-T8-8FT-2L-86W | 8 ft. General Purpose T8 | GP | T8 | 8 | 2 | 86 | 7600 | 18000 | 160 | 160 | 1 | 75000 | 0.93023 | 156.25 | 2.38 | 44.9 | 13.5%
CR-T8-4FT-4L-32W | 4 ft. Clean Room T8 | CR | T8 | 4 | 4 | 32 | 2660 | 36000 | 112 | 112 | 1 | 75000 | 0.875 | 325 | 0.31 | 32.8 | 13.5%
WL-T12-4FT-2L-40W | 4 ft. Water/Dust Resistant T12 | WL | T12 | 4 | 2 | 40 | 2910 | 20000 | 87 | 87 | 1 | 75000 | 1 | 184.25 | 0.87 | 31.45 | 9%
WL-T12-4FT-2L-60W | 4 ft. Water/Dust Resistant T12 | WL | T12 | 4 | 2 | 60 | 3320 | 12000 | 125 | 125 | 1 | 75000 | 1 | 184.25 | 1.33 | 31.45 | 9%
WL-T12-8FT-2L-75W | 8 ft. Water/Dust Resistant T12 | WL | T12 | 8 | 2 | 75 | 6110 | 12000 | 165 | 165 | 1 | 75000 | 1 | 272 | 1.33 | 64.2 | 9%
WL-T12-8FT-2L-110W | 8 ft. Water/Dust Resistant T12 | WL | T12 | 8 | 2 | 110 | 8280 | 12000 | 237 | 237 | 1 | 75000 | 1 | 272 | 2 | 64.2 | 9%
WL-T8-4FT-2L-32W | 4 ft. Water/Dust Resistant T8 | WL | T8 | 4 | 2 | 32 | 2660 | 36000 | 62 | 62 | 1 | 75000 | 0.96875 | 143.65 | 2.56 | 32.8 | 13.5%
WL-T8-8FT-2L-59W | 8 ft. Water/Dust Resistant T8 | WL | T8 | 8 | 2 | 59 | 5500 | 20000 | 110 | 110 | 1 | 75000 | 0.9322 | 237.25 | 1.31 | 44.9 | 13.5%
HB-T5HO-4FT-2L-54W | High Bay T5 High Output | HB | T5HO | 4 | 2 | 54 | 4700 | 36000 | 108 | 121 | 1 | 72000 | 1 | 194.25 | 5 | 56.7 | 14%
HB-T5HO-4FT-3L-54W | High Bay T5 High Output | HB | T5HO | 4 | 3 | 54 | 4700 | 36000 | 162 | 177 | 1 | 72000 | 1 | 194.25 | 5 | 138.55 | 14%
HB-T5HO-4FT-4L-54W | High Bay T5 High Output | HB | T5HO | 4 | 4 | 54 | 4700 | 36000 | 240 | 234 | 1 | 72000 | 1 | 194.25 | 5 | 117.25 | 14%
HB-T5HO-4FT-6L-54W | High Bay T5 High Output | HB | T5HO | 4 | 6 | 54 | 4700 | 36000 | 360 | 370 | 1 | 72000 | 1 | 233.75 | 5 | 185.25 | 14%
MS-T8-4FT-4L-28W | Motion Sensor T8 | MS | T8 | 4 | 4 | 28 | 2600 | 24000 | 193 | 193 | 2 | 72000 | 1 | 248.25 | 3.33 | 41.85 | 13.5%
MS-T5HO-4FT-4L-51W | Motion Sensor T5HO | MS | T5HO | 4 | 4 | 51 | 4700 | 36000 | 204 | 204 | 1 | 72000 | 1 | 256.25 | 0.95 | 117.25 | 14%
MS-T5HO-4FT-6L-51W | Motion Sensor T5HO | MS | T5HO | 4 | 6 | 51 | 4700 | 36000 | 306 | 306 | 1 | 72000 | 1 | 336.75 | 0.95 | 185.25 | 14%
MS-T5HO-4FT-8L-51W | Motion Sensor T5HO | MS | T5HO | 4 | 8 | 51 | 4700 | 36000 | 408 | 408 | 2 | 72000 | 1 | 348.25 | 0.95 | 117.25 | 14%
MH--FT-1L-70W | 70W Metal Halide | MH |  |  | 1 | 70 | 3500 | 12000 | 90 | 91 | 1 | 60000 | 1 | 256 | 40 | 165 | 13.25%
MH--FT-1L-100W | 100W Metal Halide | MH |  |  | 1 | 100 | 6200 | 15000 | 129 | 129 | 1 | 60000 | 1 | 256 | 42.05 | 175 | 13.25%
MH--FT-1L-175W | 175W Metal Halide | MH |  |  | 1 | 175 | 8800 | 10000 | 205 | 215 | 1 | 60000 | 1 | 256 | 26.95 | 140 | 13.25%
MH--FT-1L-250W | 250W Metal Halide | MH |  |  | 1 | 250 | 13500 | 10000 | 285 | 295 | 1 | 60000 | 1 | 256 | 28 | 140 | 13.25%
MH--FT-1L-320W | 320W Metal Halide | MH |  |  | 1 | 320 | 22500 | 20000 | 368 | 368 | 1 | 60000 | 1 | 264.625 | 89 | 175 | 13.25%
MH--FT-1L-400W | 400W Metal Halide | MH |  |  | 1 | 400 | 28000 | 20000 | 455 | 458 | 1 | 60000 | 1 | 273.25 | 42 | 180 | 13.25%
MH--FT-1L-1000W | 1000W Metal Halide | MH |  |  | 1 | 1000 | 86000 | 15000 | 1070 | 1080 | 1 | 60000 | 1 | 289 | 83 | 280 | 13.25%
CFL--FT-1L-7W | 7W Compact Fluorescent(25W) | CFL |  |  | 1 | 7 | 345 | 10000 | 7 | 7 |  |  | 1 |  | 4.83 |  | 9.75%
CFL--FT-1L-11W | 11W Compact Fluorescent(45W) | CFL |  |  | 1 | 11 | 570 | 10000 | 11 | 11 |  |  | 1 |  | 10 |  | 9.75%
CFL--FT-1L-13W | 13W Compact Fluorescent(60W) | CFL |  |  | 1 | 13 | 690 | 10000 | 13 | 13 |  |  | 1 |  | 6.7 |  | 9.75%
CFL--FT-1L-15W | 15W Compact Fluorescent | CFL |  |  | 1 | 15 | 760 | 8000 | 15 | 15 |  |  | 1 |  | 5.37 |  | 9.75%
CFL--FT-1L-20W | 20W Compact Fluorescent(75W) | CFL |  |  | 1 | 20 | 960 | 8000 | 20 | 20 |  |  | 1 |  | 15 |  | 9.75%
CFL--FT-1L-26W | 26W Compact Fluorescent(100W) | CFL |  |  | 1 | 26 | 1400 | 8000 | 26 | 26 |  |  | 1 |  | 17 |  | 9.75%
I--FT-1L-40W | 40W Incandescent | I |  |  | 1 | 40 | 505 | 1000 | 40 | 40 |  |  | 1 |  | 0.65 |  | 1.8%
I--FT-1L-60W | 60W Incandescent | I |  |  | 1 | 60 | 865 | 1000 | 60 | 60 |  |  | 1 |  | 0.63 |  | 2.067%
I--FT-1L-75W | 75W Incandescent | I |  |  | 1 | 75 | 1190 | 750 | 75 | 75 |  |  | 1 |  | 0.63 |  | 2.254%
I--FT-1L-100W | 100W Incandescent | I |  |  | 1 | 100 | 1710 | 750 | 100 | 100 |  |  | 1 |  | 0.63 |  | 2.6%
I--FT-1L-135W | 135W Incandescent | I |  |  | 1 | 135 | 2380 | 1000 | 135 | 135 |  |  | 1 |  | 1.7 |  | 2%
I--FT-1L-150W | 150W Incandescent | I |  |  | 1 | 150 | 2780 | 750 | 150 | 150 |  |  | 1 |  | 3.3 |  | 2.1%
I--FT-1L-200W | 200W Incandescent | I |  |  | 1 | 200 | 3910 | 750 | 200 | 200 |  |  | 1 |  | 3.57 |  | 2.2%
I--FT-1L-300W | 300W Incandescent | I |  |  | 1 | 300 | 5820 | 1000 | 300 | 300 |  |  | 1 |  | 11.9 |  | 2.7%
Q--FT-1L-50W | 50W Quartz | Q |  |  | 1 | 50 | 850 | 2000 | 50 | 50 |  |  | 1 |  | 13.26 |  | 3.5%
Q--FT-1L-71W | 71W Quartz | Q |  |  | 1 | 71 | 1000 | 4000 | 71 | 71 |  |  | 1 |  | 17.44 |  | 3.5%
Q--FT-1L-150W | 150W Quartz | Q |  |  | 1 | 150 | 2800 | 1500 | 150 | 150 |  |  | 1 |  | 20.15 |  | 3.5%
Q--FT-1L-250W | 250W Quartz | Q |  |  | 1 | 250 | 5000 | 200 | 250 | 250 |  |  | 1 |  | 22.25 |  | 3.5%
Q--FT-1L-500W | 500W Quartz | Q |  |  | 1 | 500 | 10300 | 2000 | 500 | 500 |  |  | 1 |  | 62.3 |  | 3.5%
Q--FT-1L-1000W | 1000W Quartz | Q |  |  | 1 | 1000 | 21500 | 2000 | 1000 | 1000 |  |  | 1 |  | 69.05 |  | 3.5%
HPS--FT-1L-100W | 100W High Pressure Sodium | HPS |  |  | 1 | 100 | 9500 | 24000 | 123 | 130 | 1 | 72000 | 1 | 169.75 | 29.5 | 189 | 17%
HPS--FT-1L-150W | 150W High Pressure Sodium | HPS |  |  | 1 | 150 | 16000 | 24000 | 175 | 188 | 1 | 72000 | 1 | 169.75 | 31.3 | 141 | 17%
HPS--FT-1L-200W | 200W High Pressure Sodium | HPS |  |  | 1 | 200 | 19800 | 24000 | 245 | 245 | 1 | 72000 | 1 | 169.75 | 59.4 | 185 | 17%
HPS--FT-1L-250W | 250W High Pressure Sodium | HPS |  |  | 1 | 250 | 25200 | 24000 | 295 | 300 | 1 | 72000 | 1 | 169.75 | 24.77 | 200 | 17%
HPS--FT-1L-400W | 400W High Pressure Sodium | HPS |  |  | 1 | 400 | 45000 | 24000 | 465 | 457 | 1 | 72000 | 1 | 184.5 | 23.68 | 360 | 17%
HPS--FT-1L-1000W | 1000W High Pressure Sodium | HPS |  |  | 1 | 1000 | 126000 | 24000 | 1102 | 1100 | 1 | 72000 | 1 | 184.5 | 92.45 | 480 | 17%
LED-T8-2FT-2L-8W | 2ft. Office T8 | LED | T8 | 2 | 2 | 8 | 1600 | 50000 | 16 | 16 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T10-2FT-2L-8W | 2ft. Office T10 | LED | T10 | 2 | 2 | 8 | 1600 | 50000 | 16 | 16 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T12-2FT-2L-8W | 2ft. Office T12 | LED | T12 | 2 | 2 | 8 | 1600 | 50000 | 16 | 16 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T8-2FT-3L-8W | 2ft. Office T8 | LED | T8 | 2 | 3 | 8 | 2400 | 50000 | 24 | 24 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T10-2FT-3L-8W | 2ft. Office T10 | LED | T10 | 2 | 3 | 8 | 2400 | 50000 | 24 | 24 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T12-2FT-3L-8W | 2ft. Office T12 | LED | T12 | 2 | 3 | 8 | 2400 | 50000 | 24 | 24 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T8-2FT-4L-8W | 2ft. Office T8 | LED | T8 | 2 | 4 | 8 | 3200 | 50000 | 32 | 32 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T10-2FT-4L-8W | 2ft. Office T10 | LED | T10 | 2 | 4 | 8 | 3200 | 50000 | 32 | 32 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T12-2FT-4L-8W | 2ft. Office T12 | LED | T12 | 2 | 4 | 8 | 3200 | 50000 | 32 | 32 | 0 | 0 | 1 | 0 | 45 | 0 | 15.3%
LED-T8-4FT-2L-15W | 4ft. T8 | LED | T8 | 4 | 2 | 15 | 3000 | 50000 | 30 | 30 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T10-4FT-2L-15W | 4ft. T10 | LED | T10 | 4 | 2 | 15 | 3000 | 50000 | 30 | 30 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T12-4FT-2L-15W | 4ft. T12 | LED | T12 | 4 | 2 | 15 | 3000 | 50000 | 30 | 30 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T8-4FT-3L-15W | 4ft. T8 | LED | T8 | 4 | 3 | 15 | 4500 | 50000 | 45 | 45 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T10-4FT-3L-15W | 4ft. T10 | LED | T10 | 4 | 3 | 15 | 4500 | 50000 | 45 | 45 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T12-4FT-3L-15W | 4ft. T12 | LED | T12 | 4 | 3 | 15 | 4500 | 50000 | 45 | 45 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T8-4FT-4L-15W | 4ft. T8 | LED | T8 | 4 | 4 | 15 | 6000 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T10-4FT-4L-15W | 4ft. T10 | LED | T10 | 4 | 4 | 15 | 6000 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T12-4FT-4L-15W | 4ft. T12 | LED | T12 | 4 | 4 | 15 | 6000 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 60 | 0 | 19.8%
LED-T8-8FT-2L-30W | 8ft. T8 | LED | T8 | 8 | 2 | 30 | 5800 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T10-8FT-2L-30W | 8ft. T10 | LED | T10 | 8 | 2 | 30 | 5800 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T12-8FT-2L-30W | 8ft. T12 | LED | T12 | 8 | 2 | 30 | 5800 | 50000 | 60 | 60 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T8-8FT-3L-30W | 8ft. T8 | LED | T8 | 8 | 3 | 30 | 8700 | 50000 | 90 | 90 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T10-8FT-3L-30W | 8ft. T10 | LED | T10 | 8 | 3 | 30 | 8700 | 50000 | 90 | 90 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T12-8FT-3L-30W | 8ft. T12 | LED | T12 | 8 | 3 | 30 | 8700 | 50000 | 90 | 90 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T8-8FT-4L-30W | 8ft. T8 | LED | T8 | 8 | 4 | 30 | 11600 | 50000 | 120 | 120 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T10-8FT-4L-30W | 8ft. T10 | LED | T10 | 8 | 4 | 30 | 11600 | 50000 | 120 | 120 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED-T12-8FT-4L-30W | 8ft. T12 | LED | T12 | 8 | 4 | 30 | 11600 | 50000 | 120 | 120 | 0 | 0 | 1 | 0 | 75 | 0 | 11.2%
LED--FT-1L-60W | 60W LED Exterior Wallpack | LED |  |  | 1 | 60 | 2700 | 50000 | 60 | 60 | 1 | 50000 | 1 | 398 | 198 | 198 | 6.6% | (150W)
LED--FT-1L-78W | 107W LED Parking Light | LED |  |  | 1 | 78 | 15816 | 50000 | 90 | 90 | 1 | 50000 | 1 | 533.75 | 267 | 267 | 7% | (250W)
LED--FT-1L-150W | 120W LED High Bay | LED |  |  | 1 | 150 | 11850 | 50000 | 165 | 165 | 1 | 50000 | 1 | 267 | 434 | 156 | 7% | (400W)

## OF & Luminous Efficiency Charts
Cree Lighting Research
| Typical Efficacy (lm/W) | Usable Optical Light (lm/W) | Luminous Efficiency
Incandescent | 17 | 10 | 58.82%
Halogen | 20 | 12 | 60%
HPL | 25 | 17 | 68%
T12 Fluourescent | 60 | 45 | 75%
Compact Fluorescent | 62 | 31 | 50%
Metal Halide | 70 | 40 | 57.14%
T8 Fluorescent | 74 | 58 | 78.38%
HPS | 91 | 50 | 54.95%
LPS | 120 | 65 | 54.17%
T5 Fluorescent | 100 | 80 | 80%
LED | 105 | 85 | 80.95%
Record LED Research | 150 | 120 | 80%
Output Factor Chart: