## Disclaimer
Disclaimer
The work described in this recommendation is a service of the Oregon State University Energy Efficiency Center (OSU EEC). This effort has been pursued as part of numerous other projects funded through multiple sources including:
• | U.S. Department of Energy’s Office of Energy Efficiency and Renewable Energy (EERE) Industrial Technologies Program and managed by Rutgers University Center for Advanced Energy Systems.
• | U.S. Department of Agriculture REAP program..
• | Oregon Processed Vegetable Commission
• | Oregon State University Sun Grant
The primary objective of the OSU EEC is to promote energy efficiency, waste minimization, and productivity in the industrial, commercial, agricultural, and residential sectors. A key strategy has included performance of energy and efficiency site assessments. This work is intended is to provide background and tools that will be helpful in identifying and evaluating potential opportunities.
We believe this recommendation to be a reasonably accurate representation of opportunities to reduce energy use, lower waste generation, and make production practices more efficient. However, because of the limited scope of our research, the Oregon State University Energy Efficiency Center cannot guarantee the accuracy, completeness, or usefulness of the information contained in this recommendation, nor assume any liability for damages resulting from the use of any information, equipment, method or process disclosed in this recommendation.
Pollution prevention recommendations are not intended to deal with the issue of compliance with applicable environmental regulations. Questions regarding compliance should be addressed to either a reputable consulting engineering firm experienced with environmental regulations or to the appropriate regulatory agency. Clients are encouraged to develop positive working relationships with regulators so that compliance issues can be addressed and resolved.
The assumptions and equations used to arrive at energy, waste, productivity, and cost savings for the opportunities are presented in this recommendation. We believe the assumptions to be conservative. If you would like to revise the assumptions you may follow the calculation methodologies presented using adjusted assumptions to develop your own revised estimates of energy, waste, productivity, and cost savings.
Please feel welcome to contact the EEC if you would like to discuss the content of this recommendation or if you have another question about energy use or pollution prevention.

## Narrative
AR No. # | [9 empty] | Revision History
Micro Hydro | [10 empty] | Template Version | 2010-10-15
[11 empty] | Recommendation Version | 2010-11-01
Recommendation | [9 empty] | Information For Narrative
[10 empty] | Energy Savings |  | Original | Rounded
Install a impulse type micro-hydro by the water storage tank. This will provide an alternative source for 44.2% of the facility’s electrical energy consumption and reduce CO2 emissions associated with electrical generation. | [10 empty] | Percent Energy Use Reduction | 0.44198 | 0.442
[11 empty] | Energy Savings (MMBtu) | 150.8484 | 151
[11 empty] | Energy Savings (therms) | 1508.4839 | 1510
[11 empty] | Energy Savings (kWh) | 44198.1818 | 44200
|  | Assessment Recommendation Summary | [8 empty] | Demand Savings (kW) |  | #NUM!
|  | Energy |  | Energy | Cost |  | Implementation | Payback |  | Other Savings
|  | (MMBtu)* |  | (kWh)* | Savings |  | Cost | (Years) |  |  | Productivity |  | #NUM!
|  | 151 |  | 44200 | 3310 |  | 7790 | 2.35 |  |  | Waste Savings |  | #NUM!
|  | * 1 MMBtu = 1,000,000 Btu, 1 kWh = 3,413 Btu | [7 empty] | Economic Results
[11 empty] | Cost Savings | 3314.8636 | 3310
[11 empty] | Implementation Cost | 7787.7727 | 7790
Background | [10 empty] | Payback | 2.3493 | 2.35
Incentives Summary
Utility companies currently supply the electrical energy for your facility. Electricity provided by utility companies is commonly generated using fossil fuels such as coal, oil, and natural gas. The combustion of these fuels releases a variety of harmful pollutants into the atmosphere; including carbon dioxide (CO2), sulfur dioxide (SO2), and nitrogen dioxide (NO2). These pollutants are the leading cause for acid rain and smog while also representing a significant portion of greenhouse gas emissions which could substantially alter the global environment. Renewable energy sources, on the other hand, are clean, naturally replenished, and will play a key role in generating a reliable energy future. | [10 empty] | REAP Incentive
BETC Incentive
Renewable BETC Incentive
ETO Incentive
[11 empty] | Net Cost | 7790
[11 empty] | Net Payback | 2.35
User Information
Hydropower is one of the most efficient and reliable renewable energy sources available. Unlike the seasonal and daily fluctuations of solar and wind energy, micro-hydro can provide constant year-round energy production with slight capacity peaks in the winter months. Micro-hydro installations typically rely on a pipe to collect water from a stream or river. The water gains energy by flowing downhill through the pipe and is then passed through a turbine connected to a generator. The type of turbine used depends on the flow characteristics available. The most common types of turbines are listed on the following page.
• | Reaction Turbine - This type of turbine is used in most large scale commercial hydro systems. A common turbine is the snail-shaped Francis turbine which is completely immersed in water and relies on the weight of the water falling onto the turbine to spin the generator. This type of turbine works well in situations where a high flow with little head is available.
• | Impulse Turbine - This type of turbine is most commonly used in small scale residential systems. A common turbine is the Pelton wheel which relies on high velocity water hitting U-shaped cups lining the perimeter of the turbine to spin the generator. Since kinetic energy (and thus velocity) is the driving force, this type of turbine works best in situations where a high head is available.
There are two major factors that affect the output capacity of hydro systems.
• | Flow - The flow is the amount of water available to power the turbine. More energy can be produced with higher flows. The size of the pipe supplying the turbine is the main limiting factor in a micro-hydro system.
• | Head - The head is the elevation change available from the source to the turbine. More energy can be produced with a larger head. This is largely limited by the water source location and the slope of the surrounding terrain. A steeper slope will require less piping to obtain the same head, decreasing associated implementation costs.
Source: http://www.flickr.com/photos/vattenfall/3592473352/
Proposal
We recommend installing 1,000 feet of 4 inch PVC pipe upstream of your water tank and using the provided flow to power an impulse type micro-hydro generator. Hydropower will reduce electricity costs and carbon emissions from electrical generation. This recommendation will save 44,200 kWh annually and result in an annual cost savings of $3,310. Take advantage of the included incentive programs for a net payback of 2.4 years after an implementation cost of $7,790.
Notes
Changing the pipe size or length will significantly change the available flow and head. We recommend consulting a specialist to determine the best sized system and turbine for your needs.
There may be local restrictions and/or permits needed to install a micro-hydro system. We did not account for these additional costs in the recommendation. We recommend consulting a specialist before implementation to review any legal restrictions.
The implementation analysis does not include any costs or rate changes associated with net metering that may instituted by your utility company.
Author |  |  | Readability Review |  |  | Engineering Review |  |  | Math Review
Mikhail Jones |  |  | Nathan Keeley |  |  | Nathan Keeley |  |  | Nathan Keeley

## Calculation
Micro Hydro
Data Collected | [5 empty] | Equations
Available Flow | [5 empty] | Eq. 1) Available Hydraulic Power (PH)
| Total Head | (H) | 150 | feet | (N. 1)
| Flow Rate | (Q) | 200 | gpm | (N. 1)
Energy Consumption Data
| Annual Energy Consumption | (ECC) | 100000 | kWh | (N. 2) | Eq. 2) System Efficiency (ηS)
Incremental Energy Data
| Incremental Energy Cost | (ICE) | 0.075 | /kWh | (N. 2)
Eq. 3) System Output Power (PO)
Assumptions
Efficiencies
| Turbine Efficiency | (ηT) | 80% |  | (N. 3) | Eq. 4) Energy Savings (ES)
| Generator Efficiency | (ηG) | 92.5% |  | (N. 4)
| Inverter Efficiency | (ηI) | 90% |  | (N. 5)
Conversion Factors | [5 empty] | Eq. 5) Cost Savings (CS)
| Time Conversion Factor | (CF1) | 8760 | hrs/yr
Available Energy Development | [5 empty] | Eq. 4) Implementation Costs (IC)
| Available Hydraulic Power | (PH) | 7.5758 | kW | (Eq. 1)
| System Efficiency | (ηS) | 66.6% |  | (Eq. 2)
| System Output Power | (PO) | 5.0455 | kW | (Eq. 3)
Notes
Energy Savings Summary | [5 empty] | N. 1) Data collected during the site assessment.
| Energy Savings | (ES) | 44198.1818 | kWh | (Eq. 4)
N. 2) Data is from utility bills found in the Site Data section.
Implementation Costs Summary
Material Costs | [5 empty] | N. 3) Turbine efficiencies typically vary between 70 and 90 percent. We assume 80 percent for this analysis.
| Pipe Length | (LP) | 1000 | ft | (N. 1)
| 4" PVC Piping Cost | (CP) | 1.65 | /ft | (Rf. 1)
| Turbine/Generator | (CM) | 1500 |  | (Rf. 2) | N. 4) Generator efficiencies typically vary between 90 and 95 percent. We assume 92.5 percent for this analysis.
| Inverter Costs | (CI) | 721 | /kW | (Rf. 3)
Labor Costs
| Labor Costs | (CL) | 1000 |  | (N. 6) | N. 5) Inverter efficiencies typically vary between 85 and 95 percent. We assume 90 percent for this analysis.
Economic Results
| Cost Savings | (CS) | 3314.8636 | /yr | (Eq. 5) | N. 6) Estimated labor cost for laying 1,000 feet of PVC.
| Implementation Costs | (IC) | 7787.7727 |  | (Eq. 6)
| Payback | (PB) | 2.3493 | yrs
References
Rf. 1) RSMean Building Construction Cost Data 2009
Rf. 2) Vendor supplied guideline for estimating turbine/generator costs.
Rf. 3) http://www.solarbuzz.com