## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# |  | 2.2621 | Process Support | None | Refrigeration Discharge Pressure | Lower the minimum ammonia condensing (discharge) pressure on the refrigeration compressors to 100 psig (63.5°F) to decrease refrigeration system energy cost by 13%. | Insert Name | Electrical Consumption | 169639.6247 | 8481.9812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 |  |  | 50
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Refrigeration Discharge Pressure
Refrigeration Discharge Pressure Template style 2015
Recommendation
Lower the minimum ammonia condensing (discharge) pressure on the refrigeration compressors to 100 psig (63.5°F) to decrease refrigeration system energy cost by 13%.
Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings
|  | Electrical Consumption |  | 169639.6247 | kWh (site) |  | 8481.9812
|  | Total |  | 578.98 | MMBtu |  | 8481.9812
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Before Incentives |  |  | 100 |  | 0.01179
|  | After Incentives |  |  | 50 |  | 0.0058948
Facility Background
The facility currently uses (insert compressor information here). During the site assessment, facility personnel explained (compressor operating conditions). (Talk about current set points). Motor information was collected for each system and is summarized in the following Motor Analysis Tool page.
Technology Background
Refrigeration discharge temperature is determined by the condenser's capacity to reject heat. When the condensing pressure goes below a minimum pressure setting, selected by operators, condenser fans turn off. This reduces condenser capacity and prevents the temperature and associated pressure from going below the set point. Compressors require less energy to operate against low discharge pressures, but to reduce this discharge pressure, the condenser fans must operate more frequently. As condenser fans typically use significantly less energy than the compressor, reducing compressor use can lead to significant energy savings. Reducing compressor discharge pressure saves approximately 1% of compressor energy consumption for each degree Fahrenheit reduction of condensing temperature.
Proposal
Adjust your minimum discharge pressure set points to 100 psig (63.5°F). Completing this procedure can be done in regular working hours by maintenance personnel so there are no implementation costs. If implemented, the recommended actions will save 169,640 kWh annually and result in an annual cost savings of $8,482 with an immediate payback.
Notes
Often there are specific applications that drive the need for high pressure set points. Below is a list of four common reasons for having such set points and how they can be fixed.
1. Liquid Injection Cooling typically consumes 5-15% of the compressor power to recompress injected refrigerant and is used to cool the compressor. Install thermosyphon oil cooling to avoid power and energy costs associated with liquid injection oil cooling. Thermosyphon cooling does not consume compressor power.
2. Expansion Device Design can lead to higher required discharge pressures. By looking into different designs, having your system evaluated and selecting components that operate well with lower discharge pressure, the efficiency of your refrigeration system can be improved.
3. Moving Refrigerant to Distant Endpoints can lead to a need for higher discharge pressures to ensure refrigerant can reach its destination. By installing liquid pumps in the system, discharge pressure can be reduced while still serving the entire refrigeration system.
4. Hot Gas Defrost is sometimes used to defrost evaporators as needed and requires a high discharge pressure. We suggest only raising the discharge pressure when needed for hot gas defrost and letting the discharge pressure drop lower otherwise, or using another defrost strategy such as applying warm process water.
Check to make sure your facility does not require high pressure set points for special applications before making alterations to your process or equipment.
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Unmodified Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
Insert Name

## Analysis
AR No. # - Analysis | [5 empty] | AR No. # - Analysis | [5 empty] | AR No. # - Analysis | [7 empty] | AR No. # - Analysis
Refrigeration Discharge Pressure Template style 2015 | [5 empty] | Refrigeration Discharge Pressure Template style 2015 | [5 empty] | Refrigeration Discharge Pressure Template style 2015 | [7 empty] | Refrigeration Discharge Pressure Template style 2015
General Data |  |  |  |  | Equations | Energy Use Summary |  |  |  |  | Equations | Compressor Energy Analysis | [7 empty] | Condenser Fan Energy Analysis
Refrigeration System Data |  |  |  |  | Eq. 1) Current Approach Temperature (TAC) | Current Conditions |  |  |  |  | Eq. 2) Total Energy Consumption (ETC,TP) | Compressor Description |  | Rated Power | Efficiency | Load Factor | Use Factor | Power Draw | Energy Use | Condenser Description |  | Quantity | Rated Power | Efficiency | Load Factor | Power Draw | Energy Use
Refrigerant Type |  | Ammonia |  | (N. 1) |  | Compressor Energy Consumption | (ECC) | 1203324.3158 | kWh | (Rf. 4) |  |  |  | (WR) (N. 1) | (ηM) (N. 1) | (LF) (Rf. 5) | (UF) (N. 1) | (PCC) (Eq. 6) | (ECC) (Eq. 7) |  |  | (QFM) (N. 1) | (WR) (N. 1) | (ηM) (N. 1) | (LF) (Rf. 5) | (PFC) (Eq. 6) | (EFT) (N. 8)
Condenser Type |  | Evaporative |  | (N. 1) |  | Fan Energy Consumption | (EFC) | 94065.3626 | kWh | (Rf. 4) | Eq. 3) Total Energy Savings (ETS) |  |  | (hp) |  |  |  | (kW) | (kWh) |  |  |  | (hp) |  |  | (kW) | (kWh)
Condenser Fan Control Type |  | On-Off |  | (N. 1) |  | Total Energy Consumption | (ETC) | 1297389.6784 | kWh | (Eq. 2) |  | Compressor #1 |  | 250 | 95% | 70% | 100% | 137.3658 | 1203324.3158 | Condenser # 1 |  | 5 | 5 | 95% | 90% | 17.6613 | 94065.3626
Operating Hours | (th) | 8760 | hrs./yr. | (N. 1) |  | Proposed Conditions |  |  |  |  | Eq. 4) Annual Cost Savings (S) | [6 empty] | - | - | [6 empty] | - | -
Current Set Points | [5 empty] | Compressor Energy Consumption | (ECP) | 991720.6598 | kWh | (Rf. 4) | [7 empty] | - | - | [6 empty] | - | -
Minimum Discharge Pressure | (pDC) | 150 | psig | (N. 1) |  | Fan Energy Consumption | (EFP) | 136029.3939 | kWh | (Rf. 4) | Eq. 5) Simple Payback (tPB) | [6 empty] | - | - | [6 empty] | - | -
Minimum Discharge Temperature | (TDC) | 84.3273 | °F | (N. 2) | Notes | Total Energy Consumption | (ETP) | 1127750.0537 | kWh | (Eq. 2) | [7 empty] | - | - | [6 empty] | - | -
Incremental Energy Data |  |  |  |  | N. 1) Refrigeration system information collected on-site during the assessment, for more details see Site Reports in the Site Data section. | Savings | [5 empty] | Totals |  | 250 |  |  |  | 137.3658 | 1203324.3158 | Totals | [5 empty] | 17.6613 | 94065.3626
Incremental Electricity Cost | (ICE) | 0.05 | /kWh | (Rf. 1) |  | Total Energy Savings | (ETS) | 169639.6247 | kWh | (Eq. 3) | Eq. 6) Power Draw (PCC,FC)
[12 empty] | Compressor Summary | [7 empty] | Condenser Fan Summary
Assumptions | [5 empty] | Economic Results | [5 empty] | Weather Bin Data |  |  | Current Discharge | Proposed Discharge | Degree Hour Savings | Percent Savings | Compressor Savings | Weather Bin Data |  |  | Current Fan Use | Proposed Fan Use | Current Fan Energy | Proposed Fan Energy | Fan Savings | Operation Hours
Proposed Set Points |  |  |  |  | N. 2) Corresponding temperature for the specified pressure and refrigerant type from thermodynamic tables. | Annual Cost Savings | (S) | 8481.9812 | /yr. | (Eq. 4) | Eq. 7) Energy Consumption (ECC) | Dry Bulb | Wet Bulb | Hours | [5 empty] | Dry Bulb | Wet Bulb | Hours
Minimum Discharge Pressure | (pDP) | 100 | psig | (N. 3) |  | Implementation Cost | (CI) | 100 |  | (N. 7) |  | (TDB) (Rf. 6) | (TWB) (Rf. 6) | (tBIN) (Rf. 6) | (TDC) (Eq. 8) | (TDP) (Eq. 8) | (HS) (Eq. 9) | (E%S) (Eq. 10) | (ECS) (Eq. 11) | (TDB) (Rf. 6) | (TWB) (Rf. 6) | (tBIN) (Rf. 6) | (UFC) (Eq. 12) | (UFP) (Eq. 12) | (EFC) (Eq. 13) | (EFP) (Eq. 13) | (EFS) (Eq. 14)
Minimum Discharge Temperature | (TDP) | 63.4634 | °F | (N. 2) |  | Simple Payback | (tPB) | 0.01179 | years | (Eq. 5) | Eq. 8) Discharge Temperature (TDC,DP) | (°F) | (°F) | (hrs./yr.) | (°F) | (°F) | (°F-hrs.) |  | (kWh) | (°F) | (°F) | (hrs./yr.) |  |  | (kWh) | (kWh) | (kWh)
Proposed Condenser System Data |  |  |  |  | N. 3) Proposed minimum discharge pressure is assumed to be the same as the measured minimum discharge pressure achieved during assessment. | [6 empty] | 112 | 73 | 0 | 94.0353 | 88 | 0 | 0% | 0 | 112 | 73 | 0 | 100% | 100% | 0 | 0 | 0 | 0
Condenser Fan Control Type |  | VSD |  |  |  | Notes | [5 empty] | 107 | 72 | 0 | 93.0353 | 87 | 0 | 0% | 0 | 107 | 72 | 0 | 100% | 100% | 0 | 0 | 0 | 0
Proposed Approach Temperature | (TAP) | 15 | °F | (N. 4) |  | N. 7) There is no implementation cost associated with plant personnel adjusting the refrigeration system discharge pressure. | [5 empty] | 102 | 71 | 3 | 92.0353 | 86 | 18.1059 | 0.002067% | 24.8713 | 102 | 71 | 3 | 100% | 100% | 52.9839 | 54.6226 | -1.6387 | 3
VSD Efficiency | (ηVSD) | 97% |  | (Rf. 2) | [7 empty] | 97 | 69 | 12 | 90.0353 | 84 | 72.4235 | 0.008268% | 99.4852 | 97 | 69 | 12 | 100% | 100% | 211.9358 | 218.4905 | -6.5547 | 12
Compressor Savings |  |  |  |  | N. 4) Proposed approach temperature is assumed the same as current approach temperature. | N. 8) Summary of energy consumption for each condenser based on the Condenser Fan Summary table analysis. On-off controlled fans energy is based on the use factor and bin operation hours to develop the actual operation hours. The actual operation hours are not shown in the analysis. VSD controlled fan energy is based on the cube of weighted average use factor, representing fan speed instead of percentage of operation hours, and total system operation hours. | [5 empty] | 92 | 68 | 41 | 89.0353 | 83 | 247.4471 | 0.02825% | 339.9076 | 92 | 68 | 41 | 100% | 100% | 724.1139 | 746.5092 | -22.3953 | 41
Compressor Energy Savings Factor | (F%S) | 1% | /°F | (Rf. 3) | [6 empty] | Eq. 9) Degree Hour Savings (HS) | 87 | 66 | 85 | 87.0353 | 81 | 513 | 0.05856% | 704.6865 | 87 | 66 | 85 | 100% | 100% | 1501.2118 | 1547.6411 | -46.4292 | 85
[12 empty] | 82 | 64 | 161 | 85.0353 | 79 | 971.6824 | 0.1109% | 1334.7591 | 82 | 64 | 161 | 100% | 100% | 2843.4718 | 2931.4143 | -87.9424 | 161
Condenser Approach Analysis |  |  |  |  | N. 5) Minimum discharge temperature difference determined by observing the system under typical loading conditions with all heat exchanger fans running at full-power. | [5 empty] | Eq. 10) Percent Savings (E%S) | 77 | 62 | 249 | 84.3273 | 77 | 1824.4909 | 0.2083% | 2506.2263 | 77 | 62 | 249 | 94.21% | 100% | 4143.1944 | 4533.678 | -390.4835 | 234.5915
Discharge Temperature | [11 empty] | 72 | 60 | 365 | 84.3273 | 75 | 3404.4545 | 0.3886% | 4676.5559 | 72 | 60 | 365 | 86.47% | 100% | 5574.0529 | 6645.7528 | -1071.7 | 315.608
Minimum Discharge Pressure | (pDM) | 134 | psig | (N. 5) | [7 empty] | 67 | 58 | 509 | 84.3273 | 73 | 5765.5818 | 0.6582% | 7919.937 | 67 | 58 | 509 | 79.9% | 100% | 7182.631 | 9267.6389 | -2085.0079 | 406.6872
Measured Discharge Temperature | (TDM) | 78.2353 | °F | (N. 2) |  | References |  |  |  |  | Eq. 11) Compressor Energy Savings (ECS) | 62 | 56 | 800 | 84.3273 | 71 | 10661.8182 | 1.217% | 14645.6907 | 62 | 56 | 800 | 74.26% | 100% | 10491.9658 | 14566.0336 | -4074.0678 | 594.0648
Weather Readings |  |  |  |  | N. 6) Dry bulb and wet bulb temperatures measured on-site at the same time minimum discharge pressures were measured. | Rf. 4) Current and proposed energy consumption values developed analysis table on following pages. | [5 empty] | 57 | 53 | 1110 | 84.3273 | 68 | 18123.2727 | 2.069% | 24895.1767 | 57 | 53 | 1110 | 67.15% | 100% | 13163.5199 | 20210.3717 | -7046.8517 | 745.3306
Dry Bulb Temperature | (TDB) | 71.1 | °F | (N. 6) | [6 empty] | Eq. 12) Fan Use Factor (UFC,FP) | 52 | 49 | 1388 | 84.3273 | 64 | 28214.2545 | 3.221% | 38756.7335 | 52 | 49 | 1388 | 59.54% | 100% | 14596.5762 | 25272.0684 | -10675.4921 | 826.4716
Wet Bulb Temperature | (TWB) | 57.2 | °F | (N. 6) |  | Rf. 5) Motor load factor developed in the previous Motor Analysis Tool (MAT) pages. | [5 empty] | 47 | 45 | 1402 | 84.3273 | 63.4634 | 29251.129 | 3.339% | 40181.0443 | 47 | 45 | 1402 | 53.49% | 100% | 13244.203 | 25526.974 | -12282.771 | 749.899
Approach Temperature | [5 empty] | Rf. 6) Weather bin data is processed using the DOE2 tool and TMY3 data from the National Solar Radiation Data Base. | [5 empty] | 42 | 40 | 1179 | 84.3273 | 63.4634 | 24598.4887 | 2.808% | 33789.9082 | 42 | 40 | 1179 | 47.45% | 89.65% | 9881.308 | 15468.1098 | -5586.8018 | 559.4888
Minimum Approach Temperature | (TAC) | 21.0353 | °F | (Eq. 1) | [7 empty] | 37 | 36 | 747 | 84.3273 | 63.4634 | 15585.302 | 1.779% | 21408.8731 | 37 | 36 | 747 | 43.53% | 76.59% | 5742.4862 | 6111.5883 | -369.1021 | 325.1449
[12 empty] | 32 | 31 | 445 | 84.3273 | 63.4634 | 9284.4169 | 1.06% | 12753.6125 | 32 | 31 | 445 | 39.45% | 64.8% | 3100.147 | 2204.3193 | 895.8277 | 175.5332
References | [11 empty] | 27 | 26 | 166 | 84.3273 | 63.4634 | 3463.4004 | 0.3954% | 4757.5274 | 27 | 26 | 166 | 36.06% | 56.15% | 1057.3239 | 535.0361 | 522.2878 | 59.8667
Rf. 1) Incremental energy costs developed in the Utility Analysis located in the Site Data section. | [10 empty] | Eq. 13) Fan Energy Consumption (EFC,FP) | 22 | 21 | 63 | 84.3273 | 63.4634 | 1314.4231 | 0.15% | 1805.5676 | 22 | 21 | 63 | 33.22% | 49.54% | 369.591 | 139.4418 | 230.1492 | 20.9266
[12 empty] | 17 | 16 | 24 | 84.3273 | 63.4634 | 500.7326 | 0.05716% | 687.8353 | 17 | 16 | 24 | 30.79% | 44.32% | 130.4935 | 38.0392 | 92.4543 | 7.3887
Rf. 2) VSD efficiencies are assumed by analysts based on Motor Tip Sheet #11, June 2008, USDOE, Industrial Technologies Program, Energy Efficiency and Renewable Energy. | [11 empty] | 12 | 11 | 8 | 84.3273 | 63.4634 | 166.9109 | 0.01905% | 229.2784 | 12 | 11 | 8 | 28.69% | 40.1% | 40.5318 | 9.389 | 31.1429 | 2.2949
[12 empty] | 7 | 7 | 1 | 84.3273 | 63.4634 | 20.8639 | 0.002382% | 28.6598 | 7 | 7 | 1 | 27.2% | 37.25% | 4.8044 | 0.94145 | 3.863 | 0.27203
[12 empty] | 2 | 2 | 1 | 84.3273 | 63.4634 | 20.8639 | 0.002382% | 28.6598 | 2 | 2 | 1 | 25.55% | 34.22% | 4.5126 | 0.72987 | 3.7827 | 0.25551
Rf. 3) Compressor energy savings factor from Industrial Refrigeration Best Practices Guide, Cascade Energy Engineering, December 2004 | [11 empty] | -3 | -2 | 1 | 84.3273 | 63.4634 | 20.8639 | 0.002382% | 28.6598 | -3 | -2 | 1 | 24.37% | 32.13% | 4.3035 | 0.60409 | 3.6994 | 0.24367
[12 empty] | -8 | -8 | 0 | 84.3273 | 63.4634 | 0 | 0% | 0 | -8 | -8 | 0 | 22.78% | 29.44% | 0 | 0 | 0 | 0
[11 empty] | Eq. 14) Fan Energy Savings (EFS) | Totals |  | 8760 |  |  | 154043.9267 | 17.58% | 211603.656 | Totals |  | 8760 |  |  | 94065.3626 | 136029.3939 | -41964.0313 | 5326.0676 | Total Operation Hours

## Incentives
3 - AR No. 1 - Incentives
Refrigeration Discharge Pressure Template style 2015
Recommendation Details
Implementation Cost |  | 100 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 8481.9812 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 0.01179 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary
Description | Incentive | After Incentive | Payback | Notes
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
| 50 |  |  |  | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 50 | 50 | 0.0058948 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.

## P-T Table
Refrigerant - Pressure/Temperature Table | [7 empty] | Pressure to Temperature Interpolation
Temp | R-11 | R-12 | R-22 | R-123 | R-134a | R-500 | Ammonia |  | Current | Proposed | Measured
-20 | - | 0.56 | 10.21 | - | - | 3.22 | 3.58 | Pressure (psig) | 150 | 100 | 134
-18 | - | 1.29 | 11.39 | - | - | 4.07 | 4.57 | Refrigerant | Temp (°F) | Temp (°F) | Temp (°F)
-16 | - | 2.04 | 12.61 | - | - | 4.96 | 5.62 | R-11 | - | - | 338.4151
-14 | - | 2.82 | 13.87 | - | 0.36 | 5.87 | 6.71 | R-12 | 116.5455 | 90.1765 | 108.85
-12 | - | 3.64 | 15.18 | - | 1.13 | 6.82 | 7.84 | R-22 | 82.6531 | 59.0811 | 75.7727
-10 | - | 4.48 | 16.54 | - | 1.94 | 7.81 | 9.02 | R-123 | - | - | 355.4257
-8 | - | 5.35 | 17.94 | - | 2.78 | 8.83 | 10.25 | R-134a | 111.4894 | 87.6111 | 104.5333
-6 | - | 6.25 | 19.39 | - | 3.66 | 9.88 | 11.54 | R-500 | 104 | 78.8824 | 96.6667
-4 | - | 7.18 | 20.89 | - | 4.56 | 10.97 | 12.87 | Ammonia | 84.3273 | 63.4634 | 78.2353
-2 | - | 8.14 | 22.44 | - | 5.51 | 12.1 | 14.26
0 | - | 9.13 | 24.04 | - | 6.48 | 13.27 | 15.7
2 | - | 10.16 | 25.69 | - | 7.5 | 14.47 | 17.2
4 | - | 11.22 | 27.4 | - | 8.55 | 15.72 | 18.76
6 | - | 12.32 | 29.16 | - | 9.64 | 17.01 | 20.38
8 | - | 13.45 | 30.97 | - | 10.77 | 18.34 | 22.05
10 | - | 14.62 | 32.85 | - | 11.95 | 19.71 | 23.8
12 | - | 15.82 | 34.78 | - | 13.16 | 21.12 | 25.6
14 | - | 17.06 | 36.77 | - | 14.41 | 22.58 | 27.48
16 | - | 18.34 | 38.82 | - | 15.71 | 24.09 | 29.42
18 | - | 19.66 | 40.94 | - | 17.06 | 25.64 | 31.43
20 | - | 21.02 | 43.11 | - | 18.45 | 27.24 | 33.51
22 | - | 22.41 | 45.35 | - | 19.88 | 28.88 | 35.66
24 | - | 23.85 | 47.65 | - | 21.37 | 30.58 | 37.9
26 | - | 25.33 | 50.03 | - | 22.9 | 32.32 | 40.2
28 | - | 26.86 | 52.46 | - | 24.48 | 34.12 | 42.59
30 | - | 28.42 | 54.97 | - | 26.11 | 35.97 | 45.05
32 | - | 30.04 | 57.55 | - | 27.8 | 37.87 | 47.6
34 | - | 31.69 | 60.2 | - | 29.53 | 39.82 | 50.23
36 | - | 33.39 | 62.92 | - | 31.33 | 41.83 | 52.95
38 | - | 35.14 | 65.71 | - | 33.17 | 43.9 | 55.76
40 | - | 36.94 | 68.58 | - | 35.08 | 46.02 | 58.65
42 | - | 38.78 | 71.53 | - | 37.04 | 48.2 | 61.64
44 | - | 40.68 | 74.55 | - | 39.06 | 50.44 | 64.72
46 | - | 42.62 | 77.65 | - | 41.13 | 52.74 | 67.9
48 | - | 44.62 | 80.83 | - | 43.27 | 55.1 | 71.17
50 | - | 46.66 | 84.09 | - | 45.47 | 57.52 | 74.54
52 | - | 48.76 | 87.4 | - | 47.74 | 60 | 78.02
54 | - | 50.91 | 90.9 | - | 50.07 | 62.55 | 81.59
56 | - | 53.12 | 94.4 | - | 52.46 | 65.16 | 85.28
58 | - | 55.38 | 98 | - | 54.92 | 67.84 | 89.1
60 | - | 57.7 | 101.7 | - | 57.45 | 70.58 | 93
62 | - | 60.07 | 105.5 | - | 60.05 | 73.4 | 97
64 | - | 62.5 | 109.3 | - | 62.72 | 76.28 | 101.1
66 | - | 64.99 | 113.3 | - | 65.46 | 79.23 | 105.3
68 | - | 67.54 | 117.3 | - | 68.27 | 82.25 | 109.7
70 | - | 70.15 | 121.5 | - | 71.16 | 85.3 | 114.2
72 | - | 72.82 | 125.7 | - | 74.12 | 88.5 | 118.8
74 | - | 75.55 | 130.1 | - | 77.16 | 91.7 | 123.5
76 | 0.32 | 78.34 | 134.5 | - | 80.28 | 95.1 | 128.4
78 | 0.92 | 81.2 | 139 | - | 83.47 | 98.5 | 133.4
80 | 1.53 | 84.13 | 143.7 | - | 86.7 | 101.9 | 138.5
82 | 2.16 | 87.1 | 148.4 | - | 90.1 | 105.5 | 143.7
84 | 2.82 | 90.2 | 153.3 | 0.59 | 93.5 | 109.1 | 149.1
86 | 3.49 | 93.3 | 158.2 | 1.21 | 97.1 | 112.8 | 154.6
88 | 4.18 | 96.5 | 163.3 | 1.85 | 100.7 | 116.6 | 160.3
90 | 4.89 | 99.7 | 168.5 | 2.51 | 104.4 | 120.5 | 166.1
92 | 5.62 | 103.1 | 173.7 | 3.19 | 108.2 | 124.4 | 172
94 | 6.37 | 106.5 | 179.1 | 3.9 | 112 | 128.5 | 178.1
96 | 7.14 | 109.9 | 184.6 | 4.62 | 116 | 132.6 | 184.4
98 | 7.94 | 113.5 | 190.3 | 5.36 | 120.1 | 136.8 | 190.8
100 | 8.76 | 117.1 | 196 | 6.13 | 124.2 | 141.1 | 197.3
102 | 9.6 | 120.8 | 201.8 | 6.92 | 128.5 | 145.5 | 204
104 | 10.46 | 124.6 | 207.8 | 7.73 | 132.8 | 150 | 210.9
106 | 11.35 | 128.4 | 213.9 | 8.57 | 137.3 | 154.5 | 217.9
108 | 12.26 | 132.3 | 220.1 | 9.43 | 141.8 | 159.2 | 225.1
110 | 13.19 | 136.3 | 226.4 | 10.31 | 146.5 | 164 | 232.5
112 | 14.15 | 140.4 | 232.9 | 11.22 | 151.2 | 168.8 | 240
114 | 15.13 | 144.6 | 239.5 | 12.15 | 156.1 | 173.8 | 247.7
116 | 16.14 | 148.8 | 246.2 | 13.11 | 161 | 178.8 | 255.5
118 | 17.18 | 153.2 | 253.1 | 14.1 | 166.1 | 183.9 | 263.6
120 | 18.24 | 157.6 | 260 | 15.11 | 171.3 | 189.2 | 271.8
122 | 19.33 | 162.1 | 267.2 | 16.15 | 176.5 | 194.5 | 280.2
124 | 20.45 | 166.7 | 274.4 | 17.22 | 181.9 | 200 | 288.8
126 | 21.59 | 171.3 | 281.8 | 18.32 | 187.5 | 205.5 | 297.6
128 | 22.77 | 176.1 | 289.3 | 19.44 | 193.1 | 211.2 | 306.6
130 | 23.97 | 180.9 | 297 | 20.59 | 198.8 | 217 | 315.7
132 | 25.2 | 185.9 | 304.8 | 21.78 | 204.7 | 222.8 | 325.1
134 | 26.46 | 190.9 | 312.7 | 22.99 | 210.7 | 228.8 | 334.6
136 | 27.75 | 196 | 320.8 | 24.24 | 216.8 | 234.9 | 344.4
138 | 29.07 | 201.2 | 329.1 | 25.51 | 223 | 241.1 | 354.3
140 | 30.42 | 206.5 | 337.5 | 26.82 | 229.4 | 247.4 | 364.5
142 | 31.81 | 211.9 | 346 | 28.16 | 235.8 | 253.8 | 374.9
144 | 33.22 | 217.4 | 354.7 | 29.53 | 242.5 | 260.4 | 385.4
146 | 34.67 | 223 | 363.6 | 30.93 | 249.2 | 267 | 396.2
148 | 36.15 | 228.7 | 372.6 | 32.37 | 256.1 | 273.8 | 407.3
150 | 37.66 | 234.5 | 381.7 | 33.84 | 263.1 | 280.7 | 418.5
152 | 39.21 | 240.4 | 391.1 | 35.35 | 270.2 | 287.7 | 429.9
154 | 40.79 | 246.4 | 400.6 | 36.89 | 277.5 | 294.9 | 441.6
156 | 42.41 | 252.5 | 410.2 | 38.47 | 285 | 302.1 | 453.5
158 | 44.06 | 258.7 | 420.1 | 40.09 | 292.5 | 309.5 | 465.7
160 | 45.75 | 265 | 430.1 | 41.74 | 300.2 | 317.1 | 478
162 | 47.48 | 271.4 | 440.3 | 43.43 | 308.1 | 324.7 | 490.6
164 | 49.24 | 278 | 450.6 | 45.15 | 316.1 | 332.5 | 503.5
166 | 51.04 | 284.6 | 461.1 | 46.92 | 324.3 | 340.4 | 516.6
168 | 52.87 | 291.3 | 471.9 | 48.72 | 332.6 | 348.5 | 529.9
170 | 54.75 | 298.2 | 482.8 | 50.57 | 341.1 | 356.7 | 543.5
172 | 56.66 | 305.2 | 493.9 | 52.45 | 349.7 | 365 | 557.4
174 | 58.61 | 312.2 | 505.1 | 54.37 | 358.5 | 373.5 | 571.5
176 | 60.61 | 319.4 | 516.6 | 56.34 | 367.5 | 382.1 | 585.8
178 | 62.64 | 326.8 | 528.3 | 58.35 | 376.6 | 390.8 | 600.5
180 | 64.71 | 334.2 | 540.2 | 60.4 | 386 | 399.7 | 615.4
182 | 66.83 | 341.7 | 552.3 | 62.49 | 395.4 | 408.8 | 630.5
184 | 68.99 | 349.4 | 564.6 | 64.62 | 405.1 | 418 | 646
186 | 71.19 | 357.2 | 577.1 | 66.81 | 414.9 | 427.4 | 661.7
188 | 73.43 | 365.1 | 589.8 | 69.03 | 425 | 436.9 | 677.7
190 | 75.72 | 373.2 | 602.8 | 71.3 | 435.2 | 446.6 | 693.9
192 | 78.05 | 381.3 | 616 | 73.62 | 445.6 | 456.5 | 710.5
194 | 80.42 | 389.6 | 629.5 | 75.98 | 456.2 | 466.5 | 727.4
196 | 82.84 | 398 | 643.2 | 78.39 | 467 | 476.7 | 744.5
198 | 85.3 | 406.6 | 657.2 | 80.84 | 478.1 | 487.1 | 762
200 | 87.8 | 415.3 | 671.4 | 83.35 | 489.3 | 497.7 | 779.7