## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# | 5 | 2.4144 | Process Support | None | Boiler Fan VFD | Install a Variable Frequency Drive (VFD) on the boiler's forced draft fan. A VFD will control the airflow by automatically adjusting fan motor speed, reducing associated annual energy consumption by 40%. | Insert Name | Electrical Consumption | 50000 | 2500 | [9 empty] | 4269 |  | N | 4219
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes | [21 empty] | Mikhail Jones
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Boiler Fan VFD
Boiler Fan VFD template style 2015
Recommendation
Install a Variable Frequency Drive (VFD) on the boiler's forced draft fan. A VFD will control the airflow by automatically adjusting fan motor speed, reducing associated annual energy consumption by 40%.
INPUT HERE!
|  | Annual Savings Summary | [6 empty] | Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings |  | Source | Quantity | Units | Cost Savings
|  | Electrical Consumption |  | 50000 | kWh (site) |  | 2500 |  | Electrical Consumption | 50000 | kWh (site) | 2500
|  | Total |  | 170.65 | MMBtu |  | 2500 |  | Total | 170.65 | MMBtu | 2500
Report Data Export page pulls values from this table
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Before Incentives |  |  | 4269 |  | 1.7076
|  | After Incentives |  |  | 4219 |  | 1.6876
Facility Background
The boiler uses a 15 hp forced draft fan with an outlet damper to control air flow. A damper controls air flow by increasing flow resistance. Partially closed dampers are inefficient because significant power is required to overcome the added resistance.
During the site assessment, facility personnel informed us that ( describe process and when airflow into boiler needs to be maximum, and when it is turned down using the damper or inlet vane.) Fan and Motor data were collected using a power quality analyzer and HOBO dataloggers. The data was analyzed using the Motor Analysis Tool (MAT) and the Fan Control Analysis Tool (FCAT).
Technology Background
Variable Frequency Drives (VFDs) vary the fan impeller speed instead of restricting airflow like a damper or inlet vane. When the boiler requires a smaller amount of air, the VFD reduces motor speed to produce the required airflow while using the least amount of energy. Likewise, it will increase motor speed as more air is demanded by the boiler. Savings are achieved by installing a VFD to reduce the electrical power required to operate the fan at specified settings. The power savings available by switching to a VFD controlled system are represented by general curves of percent loaded power versus percent loaded capacity which are found in the FCAT.
Proposal
Install a VFD on the boiler's 15 hp forced draft fan to reduce fan electrical costs. Also use a VFD bypass so the process can continue uninterrupted if the VFD fails, needs maintenance, or needs reprogramming. This will save $2,500 annually, with a $4,269 implementation cost, resulting in a 1.7 year payback.
Notes
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Unmodified Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
| Date last Modified |  | Insert Name

## Analysis
AR No. # - Analysis
Boiler Fan VFD template style 2015
Data Collected |  |  |  |  | Equations
Fan Motor Data |  |  |  |  | Analysis Equations
Boiler Fan Type | Forced Draft |  |  |  | Eq. 1) Current Energy Cost (CE,C)
Current Fan Control Type | Outlet Damper
Fan Motor Horsepower | (HP) | 15 | hp | (N. 1)
Utility Data |  |  |  |  | Eq. 2) Proposed Energy Consumption (EP)
Incremental Electricity Cost | (ICE) | 0.05 | /kWh | (Rf. 1)
Energy Analysis |  |  |  |  | Eq. 3) Proposed Energy Cost (CE,P)
Current Conditions
Current Energy Consumption | (EC) | 125000 | kWh | (Rf. 2)
Current Energy Cost | (CE,C) | 6250 | /yr. | (Eq. 1) | Eq. 4) Total Material Cost (CM,T)
Calculated Savings
Energy Savings | (ES) | 50000 | kWh | (Rf. 2)
Proposed Conditions |  |  |  |  | Eq. 5) Annual Cost Savings (S)
Proposed Energy Consumption | (EP) | 75000 | kWh | (Eq. 2)
Proposed Energy Cost | (CE,P) | 3750 | /yr. | (Eq. 3)
Eq. 6) Implementation Cost (CI)
Implementation Cost Analysis
Material Costs
VFD Equipment Cost | (CVFD) | 1559 |  | (N. 2) | Eq. 7) Simple Payback (tPB)
Manual Bypass Drive Cost | (CMBD) | 1710 |  | (N. 2)
Total Material Cost | (CM) | 3269 |  | (Eq. 4)
Labor Costs
Labor Costs | (CL) | 1000 |  | (N. 3) | References
Rf. 1) Developed in the Utility Analysis located in the Site Data section.
Economic Results
Annual Cost Savings | (S) | 2500 | /year | (Eq. 5) | Rf. 2) Developed in the Fan Control Analysis Tool (FCAT) on the following pages.
Implementation Cost | (CI) | 4269 |  | (Eq. 6)
Simple Payback | (tPB) | 1.7076 | years | (Eq. 7)
Notes
N. 1) Obtained from the equipment nameplate
N. 2) VFD Equipment Cost estimated based on prices AC Drive VFDs found at http://www.grainger.com/ Prices will vary with brand and input/output phase, amperage, and voltage.
N. 3) Estimated by analysts based on industry experience.

## Incentives
3 - AR No. 1 - Incentives
Boiler Fan VFD template style 2015
Recommendation Details
Implementation Cost |  | 4269 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 2500 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 1.7076 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary | [5 empty] | There also exists an internal incentives tracking tool:
Description | Incentive | After Incentive | Payback | Notes |  | • | Incentives spreadsheet | https://accounts.google.com/ServiceLogin?service=wise&passive=1209600&continue=https://drive.google.com/drive/folders/0BwNtS6rE2LiRfkFTbzdjWW9xSHVXbGFmb09aOVVYNG90ejhEYmtTNGF0OC1jNmk3X01NZDg&followup=https://drive.google.com/drive/folders/0BwNtS6rE2LiRfkFTbzdjWW9xSHVXbGFmb09aOVVYNG90ejhEYmtTNGF0OC1jNmk3X01NZDg#identifier
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
| 50 |  |  |  | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 50 | 4219 | 1.6876 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.

## VFD Cost Estimate Table
VFD Cost Estimate
Motor HP | VFD | Manual bypass | Labor | Total
| Equipment | w/circuit breaker | Cost | Implementation
| Cost | & 3% line reactor |  | Cost
0 | 0 | 0 | 0 | 0
0.25 | 231 | 1360 | 500 | 2091
0.5 | 239.5 | 1370 | 500 | 2109.5
0.75 | 256.5 | 1380 | 500 | 2136.5
1 | 280.25 | 1400 | 500 | 2180.25
2 | 362.75 | 1430 | 500 | 2292.75
3 | 435.5 | 1470 | 500 | 2405.5
5 | 794 | 1500 | 500 | 2794
7.5 | 1071 | 1540 | 500 | 3111
10 | 1289 | 1630 | 1000 | 3919
15 | 1559 | 1710 | 1000 | 4269
20 | 2086 | 1900 | 1000 | 4986
25 | 2285 | 1940 | 1200 | 5425
30 | 2361 | 1960 | 1200 | 5521
40 | 3585 | 2130 | 1500 | 7215
50 | 4257 | 2580 | 1800 | 8637
60 | 4550 | 2890 | 1900 | 9340
75 | 4938 | 3600 | 2000 | 10538
100 | 5526 | 4480 | 2000 | 12006
125 | 9293 | 5100 | 2000 | 16393
150 | 9300 | 6350 | 3000 | 18650
200 | 10677 | 7600 | 3000 | 21277
250 | 12063 | 8850 | 3000 | 23913
300 | 13238 | 10100 | 3000 | 26338
350 | 14413 | 11350 | 3500 | 29263
400 | 16970 | 12600 | 3500 | 33070
500 | 24447 | 13850 | 3500 | 41797
600 | 32737 | 16350 | 3500 | 52587
700 | 45463 | 18000 | 4000 | 67463
800 | 63482 | 20000 | 4000 | 87482
900 | 76492 | 22000 | 4000 | 102492
1000 | 86474 | 24000 | 4000 | 114474
Linear Interpolation Formulas
Horsepower | VSD | Bypass | Labor
15 | 1559 | 1710 | 1000