## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# |  |  |  | None | Install (Belt Type Here) | INSERT RECOMMENDED ACTIONS HERE. The use of notched v-belts will reduce motor energy use by 2.1% on average through improved transmission efficiency. This is achieved by reducing losses due to bending, friction, slip between the belt and the sheave, and stretching of the belt over time. | Insert Name | Electrical Consumption | 40779.4315 | 2038.9716 | Electrical Demand | 114.4858 | 572.4292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | N | 0
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes | [21 empty] | Mikhail Jones
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Install (Belt Type Here)
Efficient Belt Drives Template style 2015
| Recommendation | [7 empty] | <-- Make sure to customize this section.
INSERT RECOMMENDED ACTIONS HERE. The use of notched v-belts will reduce motor energy use by 2.1% on average through improved transmission efficiency. This is achieved by reducing losses due to bending, friction, slip between the belt and the sheave, and stretching of the belt over time.
INPUT HERE!
|  | Annual Savings Summary | [7 empty] | Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings |  |  | Source | Quantity | Units | Cost Savings
|  | Electrical Consumption |  | 40779.4315 | kWh (site) |  | 2038.9716 |  |  | Electrical Consumption | 40779.4315 | kWh (site) | 2038.9716
|  | Electrical Demand |  | 114.4858 | kW Months / yr |  | 572.4292 |  |  | Electrical Demand | 114.4858 | kW Months / yr | 572.4292
|  | 0 |  | 0 |  |  | 0 |  | <-- Hide
|  | 0 |  | 0 |  |  | 0 |  | <-- Hide
|  | Total |  | 139.1802 | MMBtu |  | 2611.4008 |  |  | Total | 139.1802 | MMBtu | 2611.4008
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Before Incentives |  |  | 0 |  | 0
|  | No Incentives Found |  |  | - |  | -
| Facility Background | [7 empty] | <-- Make sure to customize this section.
This paragraph should fully describe the system so that anyone who hasn't been to the facility can still understand it. Include a description of the system, operating procedures/conditions, why saving is available, how data was collected, what tools were used, and any other pertinent information.
Technology Background
| High torque, or synchronous, drive belts are similar in appearance to automotive engine timing belts. The teeth and grooves of the belt and sheave system are designed to fit together tightly to prevent slip and reduce friction. Loss in motor speed and efficiency occurs when a standard V-belt slips within the groove of the sheave. The friction between the standard V-belt and sheave generates heat within the belt, resulting in energy loss and shortening of belt life. V-belts often call for more tension than HTD belts, adding to friction and wear in bearings. Manufacturers estimate that HTD belts can improve efficiency by approximately 4% to 8% over standard V-belts. An average efficiency improvement of 5% is used in this analysis. Additional advantages include improved operation in oily and wet environments, and reduced maintenance. | [7 empty] | <-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
| HTD belts are not recommended in applications where belt slip under duress is desired. Conveyor systems are an example of an application where notched or standard V-belts are desirable instead of HTD belts. If the conveyor were to jam, a V-belt will slip and fail before damage is caused to the conveyor. | [7 empty] | <-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
| A notched belt reduces slip and allows the belt to bend around sheaves with less energy loss. Reduction in output speed and efficiency occurs when a standard V-belt slips within the groove of the sheave. Efficiency improvements have been found to range from 1% to 3%. An average efficiency improvement of 2% over standard V-belts is used in this analysis. Friction between the standard V-belt and sheave generates heat within the belt, resulting in an energy loss and shortened belt life. Notched V-belts can last twice as long as standard V-belts but have shorter lives in abrasive environments where contaminants can become trapped between the belt and the sheave. Notched V-belts may be used with existing V-belt pulleys but typically cost 20-30% more. | [7 empty] | <-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
| Proposal | [7 empty] | <-- Make sure to customize this section.
INSERT PROPOSAL STATEMENT HERE. These actions will save 40,779 kWh annually, resulting in an annual cost savings of $2,611, with a net payback period of 0.0 years after an implementation cost of $.
Notes
| With less belt friction and slip, motor applications may operate at slightly higher speeds. While a fan impeller's faster speed would move more air, for example, the fan motor's electrical draw would increase to the third power according to a fan affinity law. Continuously running equipment could nullify some of the potential savings. This can be accounted for by reducing the pulley ratios when new HTD sheaves are purchased. | [7 empty] | <-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
| HTD belts produce more noise than notched or standard V-belts because air is trapped between the fast-moving belt and toothed sheaves. For the relatively low horsepower levels of the selected motors, this added noise may not be objectionable. | [7 empty] | <-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
| An alternative to HTD belts are notched V-belts. Notched V-belts may be used for applications that cannot accept new pulleys, or where slippage during overload needs to be provided. Notched V-belts are regular V-belts with cuts manufactured in the inner surface. These cuts reduce the friction associated with a belt's flexing during use. Notched belts permit just a 1% to 3% energy savings over standard V-belts. | [7 empty] | <-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
<-- Hide This Row
| In general, we assume that the additional cost of the notched V-belts will be offset by a longer lifetime. Thus, there is no cost associated with installing notched V-belts to replace old belts when they wear out, yielding an immediate payback. No energy incentives apply to this recommendation. | [7 empty] | <-- Keep This Section
<-- Keep This Section
<-- Keep This Section
| Like standard V-belts, notched belts require periodic re-tensioning to maintain their efficiency. These calculations were done with very general assumptions based on conversations with plant personnel and general observations. Actual savings for implementation will depend on the number and size of belt driven motors. Notched V-belts should not be used on motors that cause excessive wear on the current belt as savings would be reduced by the increased replacement costs of notched V-belts. | [7 empty] | <-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
<-- Keep This Section
References
| Put any additional references here. | [7 empty] | <-- If references are used in the narrative, list them here.
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Original Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
Insert Name

## Data Preparation - Blank
AR No. # - Data Preparation
Efficient Belt Drives Template style 2015
Heading 2 |  |  |  |  | Equations
Heading 3 |  |  |  |  | Eq. 1) Equation 1 (V)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 2
Heading 3
Heading 4 | Variables | Calc | Units | (N. 1)
Heading 4 | Variables | Calc | Units | (Eq. 1)
Heading 4 | Variables | Calc | Units | (Eq. 2)
Heading 3
Heading 4 | Variables | Calc | Units | (N. 2)
Heading 4 | Variables | Calc | Units | (N. 3)

## Data Preparation - HTD
AR No. # - Data Preparation
Efficient Belt Drives Template style 2015
High Torque Drive Implementation Cost |  |  |  |  | Equations
Fixed Costs |  |  |  |  | Eq. 1) Total Fixed Cost (CFT)
Fixed Cost | (CF) | 400 | /motor | (N. 1)
Number of Motors | (n) | 30 | motors | (Rf. 1) | Eq. 2) Total Variable Cost (CVT)
Total Fixed Cost | (CFT) | 12000 |  | (Eq. 1)
Variable Costs |  |  |  |  | Eq. 3) Total Implementation Cost (CI)
Variable Cost | (CV) | 15 | /hp | (N. 1)
Total Rated Horsepower | (HPT) | 640 | hp | (Rf. 1)
Total Variable Cost | (CVT) | 9600 |  | (Eq. 2)
Total
Total Implementation Cost | (CI) | 21600 |  | (Eq. 3)
Notes
N. 1) A high torque drive system cost is based on motor horsepower and drive ratios between the motor and load. Using manufacturers' information, we have used the highest cost of each horsepower range and a variety of drive ratios to estimate associated costs. Additional labor associated with installing HTD sheaves is included in this total, which assumes implementation is delayed until the existing belts require replacement.
References
Rf. 1) Developed in Belt Replacement Inventory table on the following page.

## Drive Motor Inventory
AR No. # - Analysis | [7 empty] | <-- 650 pixels wide!
Efficient Belt Drives Template style 2015
Belt Replacement Inventory (Rf. 1)
|  | Horsepower |  | Operational | Total Current
Description | Qty | Rated | Total | Months | Power | Demand | Energy
| (n) | (HPR) | (HPT)(Eq. 1) | (tm)(N. 1) | (Pi)(N. 2) | (Di)(Eq. 2) | (Ei)(N. 2)
|  | (hp) | (hp) | (months) | (kW) | (kW-mo.) | (kWh)
Boiler FD Fan | 1 | 15 | 15 | 12 | 11.2617 | 135.1404 | 50677.6381
MH Blower 1 | 1 | 75 | 75 | 12 | 57.6149 | 691.3793 | 256386.4744
MH Blower 2 | 1 | 100 | 100 | 12 | 79.256 | 951.0726 | 352689.4086
MH Blower 3 | 1 | 150 | 150 | 12 | 116.1989 | 1394.3863 | 517084.9031
MH Blower 4 | 1 | 75 | 75 | 12 | 55.9421 | 671.3046 | 248942.1408
Dry Kiln Fans | 20 | 7.5 | 150 | 12 | 86.8054 | 1041.6652 | 303819.0133
Roof Exhaust Fan | 5 | 15 | 75 | 12 | 46.0941 | 553.1291 | 207423.4203
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
<-- Hide
Totals | 30 |  | 640 |  |  | 5438.0774 | 1937022.9986
Notes
N. 1) Number of months motor operates annually for demand savings calculations.
N. 2) Total motor power and energy. Individual motor power and energy can be found in the Motor Inventory in the Site Data section.
References
Rf. 1) Quantity, rated horsepower, total current power, and total current energy developed in the Motor Inventory pages found in the Site Data section of this report.

## Analysis
AR No. # - Analysis
Efficient Belt Drives Template style 2015
General Data |  |  |  |  | Equations | <-- (Insert --> Object --> Math Type 6.0 Equation)
Utility Data |  |  |  |  | Table Calculations
Incremental Energy Cost | (ICE) | 0.05 | /kWh | (Rf. 2) | Eq. 1) Total Horsepower (WT)
Incremental Demand Cost | (ICD) | 5 | /kW·mo. | (Rf. 2)
Eq. 2) Total Current Demand (Di)
Drive Replacement and Efficiency
Current Belt Drive |  |  |  |  | Analysis Calculations
Current Type (1st) |  | Standard V-Belts |  | (N. 1) | Eq. 3) Average Current Efficiency (ηC)
Current Efficiency (1st) | (ηC,1) | 93% |  | (Rf. 3)
Current Type (2nd) |  | N/A |  | (N. 1)
Current Efficiency (2nd) | (ηC,2) | 0% |  | (Rf. 3) | Eq. 4) Current Demand (DC)
Replacement
Replacement Fraction (1st) | (χ1) | 100% |  | (N. 2) | Eq. 5) Current Energy (EC)
Replacement Fraction (2nd) | (χ2) |  |  | (N. 2)
Weighted Efficiency |  |  |  |  | Eq. 6) Proposed Demand (DP)
Average Current Efficiency | (ηC) | 93% |  | (Eq. 3)
Proposed Belt Drive
Proposed Type |  | Notched V-Belts |  |  | Eq. 7) Proposed Energy (EP)
Proposed Efficiency | (ηP) | 95% |  | (Rf. 2)
Energy Analysis |  |  |  |  | Eq. 8) Demand Savings (DS)
Current Conditions
Current Demand | (DC) | 5438.0774 | kW·mo. | (Eq. 4) | Eq. 9) Energy Savings (ES)
Current Energy | (EC) | 1937022.9986 | kWh | (Eq. 5)
Proposed Conditions |  |  |  |  | Eq. 10) Demand Cost Savings (CSD)
Proposed Demand | (DP) | 5323.5916 | kW·mo. | (Eq. 6)
Proposed Energy | (EP) | 1896243.5671 | kWh | (Eq. 7) | Eq. 11) Energy Cost Savings (CSE)
Savings
Demand Savings | (DS) | 114.4858 | kW·mo. | (Eq. 8) | Eq. 12) Annual Cost Savings (CS)
Energy Savings | (ES) | 40779.4315 | kWh | (Eq. 9)
Cost Savings |  |  |  |  | Eq. 13) Simple Payback (tPB)
Demand Cost Savings | (SD) | 572.4292 | /yr | (Eq. 10)
Energy Cost Savings | (SE) | 2038.9716 | /yr | (Eq. 11)
References
Notes |  |  |  |  | Rf. 2) Developed in the Utility Analysis located in the Site Data section.
N. 1) Current belt type of selected motors on Belt Replacement Inventory, found on the previous page. A second belt type is chosen when combinations of standard and notched belts are installed on selected motors found in the Belt Replacement Inventory.
Rf. 3) Nominal drive efficiencies from USDOE Motor Tip Sheet #3. http://www.nrel.gov/docs/fy00osti/27833.pdf
N. 2) Percent of motor energy and demand corresponding to the selected belt type.
Economic Results |  |  |  |  | References
Annual Cost Savings | (S) | 2611.4008 | /year | (Eq. 12) | Rf. 4) Developed in the Data Preparation section for this recommendation.
Implementation Cost | (CI) | 0 |  | (Rf. 4) or (N. 3) |  | <-- Use the reference when using the "Data Preparation - HTD" page for high torque drive costs calculations.
Simple Payback | (tPB) | 0 | years | (Eq. 13) |  | <-- Use the note when recommending notched v-belts. Assume zero implementation cost unless a real current costs for v-belts can be obtained.
Notes
N. 3) Additional Cost of notched V-belts offset by longer lifetime.

## Incentives
3 - AR No. 1 - Incentives
Efficient Belt Drives Template style 2015
Recommendation Details
Implementation Cost |  | 0 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 2611.4008 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 0 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary
Description | Incentive | After Incentive | Payback | Notes
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
[5 empty] | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 0 | 0 | 0 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.

## Belt Efficiency Import
Import Data from Motor Data Collection Inventory or MATs
| Drive | Description | Qty | Rated Horsepower | Total Power | Total Energy
1 | VB | Boiler FD Fan | 1 | 15 | 11.2617 | 50677.6381
2 | VB | MH Blower 1 | 1 | 75 | 57.6149 | 256386.4744
3 | VB | MH Blower 2 | 1 | 100 | 79.256 | 352689.4086
4 | VB | MH Blower 3 | 1 | 150 | 116.1989 | 517084.9031
5 | VB | MH Blower 4 | 1 | 75 | 55.9421 | 248942.1408
6 | VB | Dry Kiln Fans | 20 | 7.5 | 86.8054 | 303819.0133
7 | VB | Roof Exhaust Fan | 5 | 15 | 46.0941 | 207423.4203
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38