## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# |  | 2.7243 | Manufacturing Process | None | Efficient Fan Blades | We recommend replacing the radial blade with a higher efficiency radial-tip fan blade in the manufacturing dust collection system. We estimate fan efficiency can be improved from the current average of 50% to a reasonable average of 70%, reducing fan operation costs by 29%. | Insert Name | Electrical Consumption | 2857.1429 | 142.8571 | Electrical Demand | 11.4286 | 685.7143 | 0 | 0 | 0 | 0 | 0 | 0 | 2400 |  | N | 2350
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Efficient Fan Blades
Recommendation template style 2015
Recommendation
We recommend replacing the radial blade with a higher efficiency radial-tip fan blade in the manufacturing dust collection system. We estimate fan efficiency can be improved from the current average of 50% to a reasonable average of 70%, reducing fan operation costs by 29%.
Annual Savings Summary
|  | Source |  | Quantity | Units |  |  | Cost Savings |  | Units Override | <-- Resource streams with "no units" can be overriden in the following cells
|  | Electrical Consumption |  | 2857.1429 | kWh (site) |  |  | 142.8571
|  | Electrical Demand |  | 11.4286 | kW Months / yr |  |  | 685.7143
<-- Hide this row!
<-- Hide this row!
|  | Total |  | 9.7514 | MMBtu |  |  | 828.5714 |  |  | <-- Make sure to convert quantity units to MMBtu for summation.
Implementation Cost Summary
|  | Description |  |  | Cost |  |  | Payback (yrs)
|  | Before Incentives |  |  | 2400 |  |  | 2.8966
|  | After Incentives |  |  | 2350 |  |  | 2.8362
Facility Background
The facility currently uses radial fan blades on the dust collection fan. During the site assessment, plant personnel informed us that the fan is a material handling fan. Motor and fan nameplate information was collected during the site assessment by energy analysts. A power quality analyzer was used to collect live power readings of the motor under typical loading conditions. A manometer was used to collect various pressure readings on either side of the fan during typical loading conditions. Motor and fan data are summarized in the following Motor Analysis Tool (MAT) and Fan Efficiency Analysis Tool (FEAT) pages.
Technology Background
Dust collection systems can be arranged in either “material-handling” or “clean-side” configurations. Material-handling fans operate with particulates flowing through the fans and use positive pressure to push the material down stream. Clean-side fans operate down stream of the bag house where no particulates flow. They use negative pressure to pull particles from the plant into a bag house.
Material-handling fans are typically centrifugal fans in which air enters the fan axially and leaves radially. Centrifugal fans operate from a combination of centrifugal forces and angular deflection of the airflow by the blades. Centrifugal fans normally produce higher static pressure than axial-flow fans of the same wheel diameter and rotational speed. The wheel is known as the impeller or rotor, which contains a back plate, shroud, and blades. Material-handling fans are used to move air containing dust and granular materials from wood and metal working operations through ducts to cyclones or bag houses. These fans can handle high temperatures (up to 800 °F), corrosive fumes and abrasive materials from cutting or grinding operations.
There are six types of centrifugal fan blades commonly used in dust collection systems. These blade types, efficiencies and characteristics are listed below.
|  |  | Radial Blade |  |  |  | Backward Inclined
|  |  | • Static efficiency to 60% |  |  |  | • Static efficiency to 80%
|  |  | • High tip speed capabilities |  |  |  | • Low-Medium tip speed capabilities
• Reasonable running clearances
• Best for erosive or sticky particulate
|  |  | Radial Tip |  |  |  | Backward Curved
|  |  | • Static efficiency to 70% |  |  |  | • Static efficiency to 83%
|  |  | • Medium-High tip speed capabilities |  |  |  | • Medium-High tip speed capabilities
|  |  | • Good for high particulate airstream |  |  |  | • Clean or dirty airstreams.
• Solid one-piece blade design
|  |  | Forward Curved (Sirocco) |  |  |  | Airfoil
|  |  | • Static efficiency to 65% |  |  |  | • Static efficiency to 87%
|  |  | • Smallest diameter wheel for a given pressure requirement |  |  |  | • Medium-High tip speed capabilities
|  |  | • High volume capability |  |  |  | • Relatively tight running clearances
• Often used for high temps
Radial type blades are most commonly used in industrial “material-handling” applications. Other types of blade configurations are prone to clogging and/or damage when material is passed through the fan. However the radial type blades have comparatively low efficiencies due to non-tangential flow conditions at the blades leading edge.
Proposal
We recommend replacing the radial blade with a higher efficiency radial-tip fan blade in the manufacturing dust collection system. Improved aerodynamics will enable the fan to move air more efficiently, reducing the power required from the fan motor, thus reducing associated annual energy consumption by 29%.
If the previously mentioned actions are taken, they will save 2,857 kWh annually and result in an annual cost savings of $829 for a net payback of 2.9 years after an implementation cost of $2,400.
Picture of fan system collected during site assessment.
Notes
Replacing fan blades often times provides a safer, and more enjoyable working environment for employees. Newer balanced fans are typically quieter and will help protect hearing and causes less fatigue and stress on employees. This may reduce the need for heavy duty ear protection and improve communication between employees.
Replacing fan blades often times reduces maintenance issues. Newer balanced fans vibrate less reducing bearing problems, stress cracking in duct work, while also reducing or eliminating the need for silencers.
| Based on |  | Data Collection | Author |  | Orange Team Review |  |  | Black Team Review
| Unmodified Template |  | Insert Name | Insert Name |  | Insert Name |  |  | Insert Name
Insert Name

## Data Preparation
AR No. # - Data Preparation
Recommendation template style 2015
Heading 2 |  |  |  |  | Equations
Heading 3 |  |  |  |  | Eq. 1) Equation 1 (V)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 2
Heading 3
Heading 4 | Variables | Calc | Units | (N. 1)
Heading 4 | Variables | Calc | Units | (Eq. 1)
Heading 4 | Variables | Calc | Units | (Eq. 2)
Heading 3
Heading 4 | Variables | Calc | Units | (N. 2)
Heading 4 | Variables | Calc | Units | (N. 3)

## Analysis
AR No. # - Analysis
Recommendation template style 2015
Data Collected |  |  |  |  | Equations | <-- (Insert --> Object --> Math Type 6.0 Equation)
Motor Data |  |  |  |  | Eq. 1) Proposed Energy Usage (EP)
Current Energy Consumption | (EC) | 10000 | kWh/yr. | (Rf. 1)
Current Power Draw | (PC) | 40 | kW | (Rf. 1)
Current Operation Months | (tM) | 12 | mo./yr. |  | Eq. 2) Proposed Power Draw (PP)
Fan Data
Current Fan Blade Type | Radial
Current Fan Efficiency | (ηC) | 50% |  | (Rf. 2) | Eq. 3) Energy Savings (ES)
Utility Data
Incremental Eergy Cost | (ICE) | 0.05 | /kWh | (Rf. 3) | Eq. 4) Power Draw Reduction (PR)
Incremental Demand Cost | (ICD) | 5 | /kW·mo. | (Rf. 3)
Eq. 5) Energy Cost Savings (CE)
Assumptions
Proposed Fan Data |  |  |  |  | Eq. 6) Power Cost Savings (CP)
Proposed Fan Blade Type | Radial-Tip
Proposed Fan Efficiency | (ηP) | 70% |  | (Rf. 4) | Eq. 7) Cost Savings (CS)
Energy Savings Analysis |  |  |  |  | Eq. 8) Implementation Costs (CI)
Proposed Energy Consumption
Proposed Energy Consumption | (EP) | 7142.8571 | kWh/yr. | (Eq. 1)
Proposed Power Draw | (PP) | 28.5714 | kW | (Eq. 2)
Energy Savings |  |  |  |  | References
Energy Savings | (ES) | 2857.1429 | kWh/yr. | (Eq. 3) | Rf. 1) Developed in the previous Motor Analysis Tool (MAT) pages.
Power Draw Reduction | (PR) | 11.4286 | kW | (Eq. 4)
Cost Savings |  |  |  |  | Rf. 2) Developed in the previous Fan Efficiency Analysis Tool (FEAT) pages.
Energy Cost Savings | (CE) | 142.8571 |  | (Eq. 5)
Power Cost Savings | (CP) | 685.7143 |  | (Eq. 6) | Rf. 3) Developed in the Utility Analysis of the Site Data section.
Implementation Cost Analysis |  |  |  |  | Rf. 4) Developed using the FSAT (Fan System Assessment Tool) software developed by the Air Movement and Control Association (AMCA) and the Oak Ridge National Laboratory for the U.S. Department of Energy's Industries of the Future program.
Material Costs
Radial-Tip Fan Cost | (CM) | 2000 |  | (Rf. 5)
Labor Costs
Labor Rate | (CLR) | 50 | /hour | (N. 1)
Installation Time | (tI) | 8 | hours | (N. 1)
Rf. 5) Grainger online catalog. http://www.grainger.com
Economic Results
Cost Savings | (CS) | 828.5714 | /yr. | (Eq. 7)
Implementation Costs | (CI) | 2400 |  | (Eq. 8) | Notes
Payback | (tPB) | 2.8966 | yrs. |  | N. 1) Energy analysts estimated material and labor costs as well as labor time. Labor rates are for facility personnel to replace fan wheels.

## Table
AR No. # - Analysis |  |  |  | <-- 650 pixels wide!
Recommendation template style 2015
Table Title (Heading 2)
Column Titles (Heading 2) | Title | Title | Title
| (ET)(N. 1) | (PT)(Eq. 1) | (ES)(Rf. 1)
| (kWh) | (kW) | (kWh)
Descriptions (Heading 4) | Input | Calc | Calc
Descriptions (Heading 4) | - | - | -
Descriptions (Heading 4) | - | - | -
Descriptions (Heading 4) | - | - | -
Totals

## Incentives
3 - AR No. 1 - Incentives
Recommendation template style 2015
Recommendation Details
Implementation Cost |  | 2400 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 828.5714 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 2.8966 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary | [5 empty] | There also exists an internal incentives tracking tool:
Description | Incentive | After Incentive | Payback | Notes |  | • | Incentives spreadsheet | https://accounts.google.com/ServiceLogin?service=wise&passive=1209600&continue=https://drive.google.com/drive/folders/0BwNtS6rE2LiRfkFTbzdjWW9xSHVXbGFmb09aOVVYNG90ejhEYmtTNGF0OC1jNmk3X01NZDg&followup=https://drive.google.com/drive/folders/0BwNtS6rE2LiRfkFTbzdjWW9xSHVXbGFmb09aOVVYNG90ejhEYmtTNGF0OC1jNmk3X01NZDg#identifier
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
| 50 |  |  |  | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 50 | 2350 | 2.8362 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.