## Narrative1
AR No. #
Freeze Tunnel Defrost
Recommendation
Use hot water to defrost the freeze tunnel which will reduce the downtime by one hour per day, allowing an increase in total annual production by pounds.
Assessment Recommendation Summary
| Cost | Implementation | Payback
| Savings | Cost | (Years)
| 1508627.9545 | 48950 | 0.032447
Background
Three times a day, a freeze tunnel is shut down and defrosted for sanitary purposes. Currently this process takes 2 hours using 65°F incoming fresh water. If the defrost water was at a higher temperature, the freeze tunnel would defrost faster, reducing downtime. It was estimated the defrost water could be steam-heated to 85°F, increasing the defrost rate and reducing the time for each defrost by ~30 min. This will allow for a longer production time by one hour per day, along with reducing annual water costs. The incoming water can be heated using direct steam injection from the steam lines currently available in the facility This will increase annual steam usage but the added income from the productivity increase will be much greater than added steam cost.
Proposal
We recommend installing steam injection on the incoming defrost water to increase the temperature to 85°F. This will reduce the defrost downtime by one hour per day, increasing annual production and income. The $1,508,628 cost savings is the increase in revenue and water cost savings after subtracting the added cost to heat the water. Installing the steam heating system will cost approximately $48,950 resulting a payback of 0.03 years.
Notes
We estimated the proposed defrost temperature to be 85°F based on conversations with the freeze tunnel manufacturer. However, be aware that hotter water can cause damage to the freeze tunnel because of the drastic change in temperature, especially if the coils are not in very good condition. Another thing to consider is the refrigeration lines. The hotter the water, the faster the boil off of any remaining liquid in the coil. So refrigeration piping and valves have to be properly designed and maintained to avoid having liquid/hydraulic hammers in the piping.

## Calculation1
Freeze Tunnel Defrost
Data Collected | [5 empty] | Equations
Steam Data | [5 empty] | Eq. 1) Defrost Time Savings (TS)
| Steam Pressure | (SP) | 125 | psi | (N. 1)
| Steam Temperature | (ST) | 350 | °F | (N. 1)
Defrost Data | [5 empty] | Eq. 2) Production Income (PI)
| Current Defrost Time | (DTC) | 6 | hrs/day | (N. 1)
| Production Rate | (PR) | 10000 | lb/hr | (N. 1)
| Current Water Temperature | (TC) | 65 | °F | (N. 1) | Eq. 3) Water Savings (WS)
| Operating Days | (OD) | 365 | days/yr | (N. 1)
Costs
| Freshwater Cost | (FC) | 0.5 | $/1000 gal | (N. 2) | Eq. 4) Water Cost Savings (WI)
| Wastewater Cost | (WC) | 1 | $/1000 gal | (N. 2)
| Income per Pound of Product | (IP) | 0.1 | $/lb | (N. 1)
| Steam Cost | (SC) | 5.25 | $/klb | (N. 2)
Eq. 5) Energy Required (ER)
Assumptions
Flow Data
| Defrost Water Flow | (F) | 30000 | gal/hr | (N. 3)
Proposed Conditions | [5 empty] | Eq. 6) Steam Required (SR)
| Proposed Defrost Time | (DTP) | 2 | hrs/day | (N. 1)
| Proposed Water Temperature | (TP) | 85 | °F | (N. 4)
Material Properties
| Density of Water | (ρ) | 8.33 | lb/gal |  | Eq. 7) Cost to Heat Water (HW)
| Specific Heat of Water | (CP) | 1 | Btu/lbm-°F
| Steam Enthalpy (Evap at 150 psig) | (E) | 857 | Btu/lb
Conversion Factors
| Energy Conversion Factor | (CF1) | 1000000 | Btu/MMBtu
Notes
Production Income | [5 empty] | N. 1) Data provided by plant personnel.
| Defrost Time Savings | (TS) | 4 | hr/day | (Eq. 1) | N. 2) Costs according to utility bills.
| Production Income | (PI) | 1460000 |  | (Eq. 2) | N. 3) 75% of total water usage based on assumptions by plant personnel.
Water Savings Income | [5 empty] | N. 4) Manufacturer's recommended maximum defrost water temperature of 90-100°F. Also note that refrigeration piping and valves may have to be replaced to avoid having liquid/hydraulic hammer in the piping.
| Water Savings | (WS) | 43800000 | gal/yr | (Eq. 3)
| Water Cost Savings | (WI) | 65700 |  | (Eq. 4)
Water Heating Cost
| Energy Required | (ER) | 3648.54 | MMBtu | (Eq. 5)
| Steam Required | (SR) | 3251818.1818 | lbs | (Eq. 6)
| Cost to Heat Water | (HW) | 17072.0455 |  | (Eq. 7)

## Calculation2
Freeze Tunnel Defrost
Implementation Costs Summary | [5 empty] | Equations | Information For Narrative
Material Costs | [5 empty] | Eq. 8) Material Costs (MT) | Percent Energy Use Reduction
| Pipe Cost per foot | (MP) | 6 | /ft | (Rf. 5) |  | Energy (MMBtu)
| Insulation Cost per foot | (MI) | 8 | /ft | (Rf. 5) |  | Energy (kWh) | 0
| Piping Distance | (D) | 100 | ft |  | Eq. 9) Labor Costs (LT) | Cost Savings | 1508627.9545
| Steam Injector | (SI) | 45000 |  | (Rf. 6) |  | Implementation Cost | 48950
| Material Costs | (MT) | 46400 |  | (Eq. 8) |  | Payback | 0.032447
Labor Costs | [5 empty] | Eq. 10) Cost Savings (CS)
| Labor Rate | (LR) | 42.5 | /hr | (Rf. 5)
| Labor Hours | (LH) | 60 | hrs | (Rf. 5)
| Labor Costs | (LT) | 2550 |  | (Eq. 9) | Eq. 11) Implementation Costs (IC)
Economic Results
| Cost Savings | (CS) | 1508627.9545 | /yr | (Eq. 10)
| Implementation Costs | (IC) | 48950 |  | (Eq. 11)
| Payback | (PB) | 0.032447 | yrs
References
Rf. 5) RSMeans Mechanical Cost Data 2006
Rf. 6) Vendor quote for a stainless steel Direct Steam Injection system including all valves, gauges, steam lines, and electronic temperature controller.

## Steam Table
Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy
|  |  | Saturated Liquid | Evaporated | Saturated Vapor
(psig) | (°F) | (ft3/lb) | (Btu/lb) | (Btu/lb) | (Btu/lb)
25 (vacuum) | 134 | 142 | 102 | 1017 | 1119
20 (vacuum) | 162 | 73.9 | 129 | 1001 | 1130
15 (vacuum) | 179 | 51.3 | 147 | 990 | 1137
10 (vacuum) | 192 | 39.4 | 160 | 982 | 1142
5 (vacuum) | 203 | 31.8 | 171 | 976 | 1147
0 | 212 | 26.8 | 180 | 970 | 1150
1 | 215 | 25.2 | 183 | 968 | 1151
2 | 219 | 23.5 | 187 | 966 | 1153
3 | 222 | 22.3 | 190 | 964 | 1154
4 | 224 | 21.4 | 192 | 962 | 1154
5 | 227 | 20.1 | 195 | 960 | 1155
6 | 230 | 19.4 | 198 | 959 | 1157
7 | 232 | 18.7 | 200 | 957 | 1157
8 | 233 | 18.4 | 201 | 956 | 1157
9 | 237 | 17.1 | 205 | 954 | 1159
10 | 239 | 16.5 | 207 | 953 | 1160
12 | 244 | 15.3 | 212 | 949 | 1161
14 | 248 | 14.3 | 216 | 947 | 1163
16 | 252 | 13.4 | 220 | 944 | 1164
18 | 256 | 12.6 | 224 | 941 | 1165
20 | 259 | 11.9 | 227 | 939 | 1166
22 | 262 | 11.3 | 230 | 937 | 1167
24 | 265 | 10.8 | 233 | 934 | 1167
26 | 268 | 10.3 | 236 | 933 | 1169
28 | 271 | 9.85 | 239 | 930 | 1169
30 | 274 | 9.46 | 243 | 929 | 1172
32 | 277 | 9.1 | 246 | 927 | 1173
34 | 279 | 8.75 | 248 | 925 | 1173
36 | 282 | 8.42 | 251 | 923 | 1174
38 | 284 | 8.08 | 253 | 922 | 1175
40 | 286 | 7.82 | 256 | 920 | 1176
42 | 289 | 7.57 | 258 | 918 | 1176
44 | 291 | 7.31 | 260 | 917 | 1177
46 | 293 | 7.14 | 262 | 915 | 1177
48 | 295 | 6.94 | 264 | 914 | 1178
50 | 298 | 6.68 | 267 | 912 | 1179
55 | 300 | 6.27 | 271 | 909 | 1180
60 | 307 | 5.84 | 277 | 906 | 1183
65 | 312 | 5.49 | 282 | 901 | 1183
70 | 316 | 5.18 | 286 | 898 | 1184
75 | 320 | 4.91 | 290 | 895 | 1185
80 | 324 | 4.67 | 294 | 891 | 1185
85 | 328 | 4.44 | 298 | 889 | 1187
90 | 331 | 4.24 | 302 | 886 | 1188
95 | 335 | 4.05 | 305 | 883 | 1188
100 | 338 | 3.89 | 309 | 880 | 1189
105 | 341 | 3.74 | 312 | 878 | 1190
110 | 344 | 3.59 | 316 | 875 | 1191
115 | 347 | 3.46 | 319 | 873 | 1192
120 | 350 | 3.34 | 322 | 871 | 1193
125 | 353 | 3.23 | 325 | 868 | 1193
130 | 356 | 3.12 | 328 | 866 | 1194
135 | 358 | 3.02 | 330 | 864 | 1194
140 | 361 | 2.92 | 333 | 861 | 1194
145 | 363 | 2.84 | 336 | 859 | 1195
150 | 366 | 2.74 | 339 | 857 | 1196
155 | 368 | 2.68 | 341 | 855 | 1196
160 | 371 | 2.6 | 344 | 853 | 1197
165 | 373 | 2.54 | 346 | 851 | 1197
170 | 375 | 2.47 | 348 | 849 | 1197
175 | 377 | 2.41 | 351 | 847 | 1198
180 | 380 | 2.31 | 353 | 845 | 1198
185 | 382 | 2.29 | 355 | 843 | 1198
190 | 384 | 2.24 | 358 | 841 | 1199
195 | 386 | 2.19 | 360 | 839 | 1199
200 | 388 | 2.14 | 362 | 837 | 1199
205 | 390 | 2.09 | 364 | 836 | 1200
210 | 392 | 2.05 | 366 | 834 | 1200
215 | 394 | 2 | 368 | 832 | 1200
220 | 396 | 1.96 | 370 | 830 | 1200
225 | 397 | 1.92 | 372 | 828 | 1200
230 | 399 | 1.89 | 374 | 827 | 1201
235 | 401 | 1.85 | 376 | 825 | 1201
240 | 403 | 1.81 | 378 | 823 | 1201
245 | 404 | 1.78 | 380 | 822 | 1202
250 | 406 | 1.75 | 382 | 820 | 1202
255 | 408 | 1.72 | 383 | 819 | 1202
260 | 409 | 1.69 | 385 | 817 | 1202
265 | 411 | 1.66 | 387 | 815 | 1202
270 | 413 | 1.63 | 389 | 814 | 1203
275 | 414 | 1.6 | 391 | 812 | 1203
280 | 416 | 1.57 | 392 | 811 | 1203
285 | 417 | 1.55 | 394 | 809 | 1203
290 | 418 | 1.53 | 395 | 808 | 1203
295 | 420 | 1.49 | 397 | 806 | 1203
300 | 421 | 1.47 | 398 | 805 | 1203
305 | 423 | 1.45 | 400 | 803 | 1203
310 | 425 | 1.43 | 402 | 802 | 1204
315 | 426 | 1.41 | 404 | 800 | 1204
320 | 427 | 1.38 | 405 | 799 | 1204
325 | 429 | 1.36 | 407 | 797 | 1204
330 | 430 | 1.34 | 408 | 796 | 1204
335 | 432 | 1.33 | 410 | 794 | 1204
340 | 433 | 1.31 | 411 | 793 | 1204
345 | 434 | 1.29 | 413 | 791 | 1204
350 | 435 | 1.28 | 414 | 790 | 1204
355 | 437 | 1.26 | 416 | 789 | 1205
360 | 438 | 1.24 | 417 | 788 | 1205
365 | 440 | 1.22 | 419 | 786 | 1205
370 | 441 | 1.2 | 420 | 785 | 1205
375 | 442 | 1.19 | 421 | 784 | 1205
380 | 443 | 1.18 | 422 | 783 | 1205
385 | 445 | 1.16 | 424 | 781 | 1205
390 | 446 | 1.14 | 425 | 780 | 1205
395 | 447 | 1.13 | 427 | 778 | 1205
400 | 448 | 1.12 | 428 | 777 | 1205
450 | 460 | 1 | 439 | 766 | 1205
500 | 470 | 0.89 | 453 | 751 | 1204
550 | 479 | 0.82 | 464 | 740 | 1204
600 | 489 | 0.74 | 475 | 728 | 1203
650 | 497 | 0.69 | 483 | 719 | 1202
700 | 505 | 0.64 | 491 | 710 | 1201
750 | 513 | 0.6 | 504 | 696 | 1200
800 | 520 | 0.56 | 512 | 686 | 1198
900 | 534 | 0.49 | 529 | 666 | 1195
1000 | 546 | 0.44 | 544 | 647 | 1191
1250 | 574 | 0.34 | 580 | 600 | 1180
1500 | 597 | 0.23 | 610 | 557 | 1167
1750 | 618 | 0.22 | 642 | 509 | 1151
2000 | 636 | 0.19 | 672 | 462 | 1134
2250 | 654 | 0.16 | 701 | 413 | 1114
2500 | 669 | 0.13 | 733 | 358 | 1091
2750 | 683 | 0.11 | 764 | 295 | 1059
3000 | 696 | 0.08 | 804 | 213 | 1017