## Narrative1
AR No. #
Insulate Greenhouse
Recommendation
Install clear, corrugated high density polyethylene insulation on greenhouse walls to reduce heat loss. This will reduce associated heat loss from the walls by 7.5% and reduce boiler fuel use by 17.7%.
Assessment Recommendation Summary
| Energy | Cost | Implementation | Payback
| (MMBtu)* | Savings | Cost | (Years)
| 883.8 | 13257 | 29062.5 | 2.1922
* 1,000,000 Btu = 1 MMBtu
Background
Un-insulated or poorly insulated walls are a significant source of energy loss in any greenhouse. Temperature differentials between the walls and surroundings act as a driving force for the heat transfer between these bodies. The rate of this heat transfer is directly proportional to the magnitude of the temperature differential. This differential creates a steady energy stream exiting the greenhouse, requiring the boiler to consume more energy to replenish the lost heat. Insulating greenhouse walls will decrease this rate of heat transfer thus saving energy and increasing available heat from heaters, improving the efficiency of the system.

## Narrative2
Proposal
We recommend replacing current fiber reinforced plastic with corrugated high density polyethylene insulation on greenhouse walls to reduce heat loss. This will result in a cost savings of $13,257 and a 17.7% reduction in energy use for the greenhouse. There is an implementation cost of $29,063, resulting in a payback of 2.2 years.
Source: http://www.flickr.com/photos/simeon_barkas/

## Calculation1
Insulate Greenhouse
| Data Collected | [5 empty] | Equations
| Dimensional Data | [5 empty] | Eq. 1) Current Roof R-Value (RCR)
|  | Greenhouse Roof Surface Area | (SR) | 100000 | ft2 | (N. 1)
|  | Greenhouse Wall Surface Area | (SW) | 15000 | ft2 | (N. 1)
| Energy Consumption Data | [5 empty] | Eq. 2) Proposed Roof R-Value (RPR)
|  | Annual Boiler Energy Consumption | (ECB) | 5000 | MMBtu | (N. 2)
Incremental Energy Data
|  | Incremental Boiler Fuel Cost | (ICN) | 15 | /MMBtu | (N. 3) | Eq. 3) Current Wall R-Value (RCW)
Assumptions
| Efficiencies | [5 empty] | Eq. 4) Proposed Wall R-Value (RPW)
|  | Boiler Efficiency | (ηB) | 75 | % | (Rf. 1)
Environmental Conditions
|  | Heating Degree Days | (HD) | 7500 | °F-days/yr | (Rf. 2)
| Material Properties | [5 empty] | References
|  | Fiber Reinforced Plastic R-Value | (RC1) | 0.83 |  | (N. 4)(Rf. 3) | Rf. 1) This is the average boiler efficiency that we observed during our site visit. However, we recommended that you have your boiler(s) tuned, which would increase the efficiency. If this action is taken, it will result in a slightly lower cost savings for this recommendation.
|  | Double Layer Polyethylene R-Value | (RC2) | 1.5 |  | (N. 4)(Rf. 4)
|  | Corrugated Polyethylene R-Value | (RP) | 2.3 |  | (N. 4)(Rf. 5)
|  | Internal Film Resistance R-Value | (RIV) | 0.68 |  | (N. 4)(N. 5)(Rf. 6)
|  | Internal Film Resistance R-Value | (RIS) | 0.62 |  | (N. 4)(N. 6)(Rf. 6)
|  | External Film Resistance R-Value | (RE) | 0.31 |  | (N. 4)(N. 7)(Rf. 6)
Conversion Factors
|  | Energy Conversion Factor | (CF1) | 1000000 | Btu/MMBtu |  | Rf. 2) Heating degree days from www.degreedays.net
|  | Time Conversion Factor | (CF2) | 24 | hrs/day
Rf. 3) Current wall insulation R-Value from http://attra.ncat.org
R-Value Development
|  | Current Roof R-Value | (RCR) | 2.43 |  | (N. 4)(Eq. 1) | Rf. 4) Current roof insulation R-Value from http://attra.ncat.org
|  | Proposed Roof R-Value | (RPR) | 2.43 |  | (N. 4)(Eq. 2)
|  | Current Wall R-Value | (RCW) | 1.82 |  | (N. 4)(Eq. 3) | Rf. 5) Proposed wall insulation R-Value from http://solexx.com/
|  | Proposed Wall R-Value | (RPW) | 3.29 |  | (N. 4)(Eq. 4)
Rf. 6) ASHRAE Handbook of Fundamentals 1997
Notes
N. 1) Lengths and angles were measured during the site assessment.
N. 2) Annual boiler fuel consumption based on boiler operating charateristics.
N. 3) Incremental boiler fuel cost from utility bills.
N. 4) R-value units are in (ft2-oF-hr/Btu).
N. 5) For still air on a vertical surface with a horizontal direction of heat flow.
N. 6) For still air on a 45o sloping surface with a upward direction of heat flow.
N. 7) For moving air with a average velocity of 1.8 mph.

## Calculation2
Insulate Greenhouse
| Energy Savings Summary | [5 empty] | Equations | Information For Narrative
|  | Current Annual Heat Loss | (QLC) | 8890.9239 | MMBtu | (Eq. 5) | Eq. 5) Current Heat Loss (QLC) | Percent Heat Loss Reduction | 7.5
|  | Annual Solar Heat Gain | (QSG) | 3890.9239 | MMBtu | (Eq. 6) |  | Percent Energy Use Reduction | 17.7
|  | Proposed Annual Heat Loss | (QLP) | 8228.0761 | MMBtu | (Eq. 7) |  | Energy (MMBtu) | 883.8
|  | Annual Energy Savings | (ES) | 883.7971 | MMBtu | (Eq. 8) |  | Energy (therms) | 8838
[7 empty] | Eq. 6) Solar Heat Gain (QSG) | Cost Savings | 13257
| Implementation Costs Summary | [6 empty] | Implementation Cost | 29063
| Material Costs | [6 empty] | Payback | 2.2
|  | Insulation Cost | (CI) | 1.8125 | /ft2 | (Rf. 5) | Eq. 7) Proposed Heat Loss (QLP)
|  | Material Costs | (CM) | 27187.5 |  | (Eq. 9) |  | Furture Improvements
| Labor Costs | [6 empty] | Add opacity material properties and calculate new solar gain
|  | Labor Rate | (LR) | 50 | /hr | (Rf. 5)
|  | Labor Hours | (LH) | 0.0025 | hr/ft2 | (Rf. 5) | Eq. 8) Energy Savings (ES)
|  | Labor Costs | (CL) | 1875 |  | (Eq. 10)
Economic Results
|  | Cost Savings | (CS) | 13256.9558 | /yr | (Eq. 11) | Eq. 9) Material Costs (CM)
|  | Implementation Costs | (IC) | 29062.5 |  | (Eq. 12)
|  | Payback | (PB) | 2.1922 | yrs
Eq. 10) Labor Costs (CL)
References
Rf. 5) RSMean Building Construction Cost Data 2009
Eq. 11) Cost Savings (CS)
Eq. 12) Implementation Costs (IC)