## Database Export
Assessment Recommendations
AR Number | Number of Pages | ARC Code | APP Code | BP Tool Used | AR Name | AR Description | AR Author | Primary Savings Source | Primary Savings Quantity | Primary Cost Savings | Secondary Savings Source | Secondary Savings Quantity | Secondary Cost Savings | Tertiary Savings Source | Tertiary Savings Quantity | Tertiary Cost Savings | Quaternary Savings Source | Quaternary Savings Quantity | Quaternary Cost Savings | Implementation Cost | Other Cost | Incremental | Implementation Cost After Incentives
# | 4 | 2.2626 | Process Support | None | Refrigeration Suction Pressure | Adjust refrigeration suction pressure set points from 24.0 psig (10.2°F) to 34.0 psig (20.5°F). This will increase system efficiency, decreasing compressor energy consumption by 20%. | Insert Name | Electrical Consumption | 251009.538 | 12550.4769 | Electrical Demand | 343.8487 | 1719.2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | N | 0
Resource Streams
Source Name | Source Code | Units
Electrical Consumption | EC | kWh (site)
Electrical Demand | ED | kW Months / yr
Other Electrical Fees | EF | no units
Natural Gas | E2 | MMBtu
L.P.G. | E3 | MMBtu
#1 Fuel Oil | E4 | MMBtu
#2 Fuel Oil | E5 | MMBtu
#4 Fuel Oil | E6 | MMBtu
#6 Fuel Oil | E7 | MMBtu
Coal | E8 | MMBtu
Wood | E9 | MMBtu
Paper | E10 | MMBtu
Other Gas | E11 | MMBtu
Other Energy | E12 | MMBtu
Water Disposal | W1 | Gallons
Other Liquid (non-haz) | W2 | Gallons
Other Liquid (haz) | W3 | Gallons
Solid Waste (non-haz) | W4 | Pounds
Solid Waste (haz) | W5 | Pounds
Gaseous Waste | W6 | Pounds
Personnel Changes | R1 | no units
Administrative Costs | R2 | no units
Primary Raw Material | R3 | no units
Ancillary Material Cost | R4 | no units
Water Consumption | R5 | no units
One-time Revenue | R6 | no units
Primary Product | P1 | no units
By-product Production | P2 | no units
Increase in Production | P3 | %
Application Codes
Application | APP Code | Examples
Manufacturing Process | 1 | Process Heat Recovery, Variable Speed Drives on Process Equipment, Solvent Recovery
Process Support | 2 | Air Compressors, Steam, Nitrogen, Cogeneration
Building and Grounds | 3 | Lights, HVAC, Burn Waste for Heat
Administrative | 4 | Taxes, Inventory Control, Sale of Wastes
Production Units
Display Units | Rutgers Units
Not Available | Not Available
Pieces | Pieces
Pounds | Pounds
Tons | Tons
BBL | BBL
1000's Gallons | Thousand Gallons
1000's ft./sq. ft. | Thousand Feed or Thousand Square Feet
Bushels | Bushels
BP Tools
Tool Name | Tool Desciption
None | None
AM+ | AirMaster+
CWSAT | Chilled Water System Analysis Tool
FSAT | Fan System Assessment Tool (FSAT)
MM+ | MotorMaster+ 4.0
NxEAT | Nox and Energy Assessment Tool
PHAST | Process Heating Assessment Tool (PHAST)
PSAT | Pump System Assessment Tool (PSAT)
SSTS | Steam System Tool Suite (SSST/SSAT/3E+)
ASD | ASDMaster: Adjustable Speed Drive Evaluation Tool

## Narrative
AR No. # - Refrigeration Suction Pressure
Suction Pressure Template style 2015
Recommendation
Adjust refrigeration suction pressure set points from 24.0 psig (10.2°F) to 34.0 psig (20.5°F). This will increase system efficiency, decreasing compressor energy consumption by 20%.
Annual Savings Summary
|  | Source |  | Quantity | Units |  | Cost Savings
|  | Electrical Consumption |  | 251009.538 | kWh (site) |  | 12550.4769
|  | Electrical Demand |  | 343.8487 | kW Months / yr |  | 1719.2434
|  | Total |  | 856.6956 | MMBtu |  | 14269.7203
Implementation Cost Summary
|  | Description |  |  | Cost |  | Payback (yrs)
|  | Before Incentives |  |  | 0 |  | 0
|  | No Incentives Found |  |  | - |  | -
Facility Background
The facility currently uses (insert compressor information here). During the site assessment, facility personnel explained (compressor operating conditions). (Talk about current set points). Motor information was collected for each system and is summarized in the following Motor Analysis Tool page.
Technology Background
Refrigerant evaporation temperature is directly related to compressor suction pressure. Compressors require less power and energy to operate if the pressure differential between suction and discharge pressure (lift) is reduced. Raising suction pressure increases refrigeration efficiency by decreasing this lift and the compression ratio (discharge pressure divided by suction pressure). Typically, 2% to 3% of refrigeration compressor energy can be saved for each degree Fahrenheit increase in suction temperature and associated suction pressure.
Proposal
Change the suction pressure setpoints on the refrigeration system's controllers. Completing this procedure can be done in regular working hours by maintenance personnel so that there are no implementation costs. These actions will decrease the compression ratio, reducing associated annual energy consumption by 251,010 kWh, resulting in an annual cost savings of $14,270.
Notes
Put any additional notes or references at the end. Things like alternative proposals, considerations, and potentials problems or side-effects should all be noted.
| Based on |  | Data Collection | Author |  | Orange Team Review |  | Black Team Review
| Unmodified Template |  | Insert Name | Insert Name |  | Insert Name |  | Insert Name
Insert Name

## Data Preparation
AR No. # - Data Preparation
Suction Pressure Template style 2015
Heading 2 |  |  |  |  | Equations
Heading 3 |  |  |  |  | Eq. 1) Equation 1 (V)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 4 | Variables | Input | Units | (Rf. 1)
Heading 2
Heading 3
Heading 4 | Variables | Calc | Units | (N. 1)
Heading 4 | Variables | Calc | Units | (Eq. 1)
Heading 4 | Variables | Calc | Units | (Eq. 2)
Heading 3
Heading 4 | Variables | Calc | Units | (N. 2)
Heading 4 | Variables | Calc | Units | (N. 3)

## Analysis
AR No. # - Analysis | [5 empty] | AR No. # - Analysis
Suction Pressure Template style 2015 | [5 empty] | Suction Pressure Template style 2015
Data Collected |  |  |  |  | Equations | Compressor Summary
Refrigeration System Data |  |  |  |  | Analysis Equations | Description | Rated Power | Operation Hours | Operation Months | Input Power | Current Demand | Current Energy | Demand Savings | Energy Savings
Refrigerant Type |  | Ammonia |  |  | Eq. 1) Temperature Differential (ΔT(C,P))
Cooled Medium Target Temperature | (TT) | 35 | °F |  |  |  | (WR) (N. 1) | (tH) (N. 1) | (tM) (N. 1) | (PC) (N. 4) | (DC) (Eq. 6) | (EC) (Eq. 7) | (DS) (Eq. 8) | (ES) (Eq. 9)
Current Conditions |  |  |  |  | Eq. 2) Suction Temperature Increase (ΔT) |  | (hp) | (hrs./yr.) | (mo./yr.) | (kW) | (kW·mo.) | (kWh) | (kW·mo.) | (kWh/yr.)
Current Suction Pressure Set Point | (pC) | 24 | psig | (N. 1) |  | Compressor No. 1 | 100 | 8760 | 12 | 70 | 840 | 613200 | 171.9243 | 125504.769
Current Suction Temperature Set Point | (TC) | 10.2222 | °F | (N. 2) | Eq. 3) Energy Cost Savings (CSE) | Compressor No. 2 | 100 | 8760 | 12 | 70 | 840 | 613200 | 171.9243 | 125504.769
Current Temperature Differential | (ΔTC) | 24.7778 | °F | (Eq. 1) | [6 empty] | - | - | - | -
Proposed Conditions |  |  |  |  | Eq. 4) Demand Cost Savings (CSD) | [5 empty] | - | - | - | -
Proposed Suction Pressure | (pP) | 34 | psig | (N. 1) | [6 empty] | - | - | - | -
Proposed Suction Temperature | (TP) | 20.4558 | °F | (N. 2) | Eq. 5) Cost Savings (CS) | Totals | 200 |  |  | 140 | 1680 | 1226400 | 343.8487 | 251009.538
Proposed Temperature Differential | (ΔTP) | 14.5442 | °F | (Eq. 1)
Incremental Cost Data |  |  |  |  | Table Equations | Notes
Incremental Electricity Cost | (ICE) | 0.05 | /kWh | (Rf. 1) | Eq. 6) Current Demand (DC) | N. 4) Motor power obtained from the Motor Analysis Tool (MAT) on the previous pages.
Incremental Demand Cost | (ICD) | 5 | /kW·mo. | (Rf. 1)
Eq. 7) Current Energy (EC)
Compressor Analysis
Savings |  |  |  |  | Eq. 8) Demand Savings (DS)
Savings Factor | (F%S) | 2% | /°F | (N. 3)
Suction Temperature Increase | (ΔT) | 10.2336 | °F | (Eq. 2) | Eq. 9) Energy Savings (ES)
Energy Savings
Current Energy | (EC) | 1226400 | kWh/yr. | (Rf. 2)
Energy Savings | (ES) | 251009.538 | kWh/yr. | (Rf. 2) | References
Energy Cost Savings | (CSE) | 12550.4769 | /yr. | (Eq. 3) | Rf. 1) Incremental energy costs developed in the Utility Analysis of the Site Data section.
Demand Savings
Current Demand | (DC) | 1680 | kW·mo. | (Rf. 2) | Rf. 2) Demand and energy values developed in the Compressor Summary Table on the following page.
Demand Savings | (DS) | 343.8487 | kW·mo. | (Rf. 2)
Demand Cost Savings | (CSD) | 1719.2434 | /yr. | (Eq. 4)
Rf. 3) Adjusting suction pressure can be done in regular working hours by maintenance personnel so there are no implementation costs
Economic Results
Cost Savings | (CS) | 14269.7203 | /yr. | (Eq. 5)
Implementation Cost | (CI) | 0 |  | (Rf. 3)
Payback | (tPB) | 0 | yrs.
Notes
N. 1) Data collected on-site during the assessment. See analyst site report for details.
N. 2) Saturated refrigerant temperature at corresponding pressure.
N. 3) An industry accepted value to determine compressor energy. (2% of compressor energy saved for each degree Fahrenheit that suction temperature increases).

## Incentives
3 - AR No. 1 - Incentives
Suction Pressure Template style 2015
Recommendation Details
Implementation Cost |  | 0 |  |  |  | Step 1: Look up possible incentives. Possible resources include but are not limited to:
Annual Cost Savings |  | 14269.7203 | /year |  |  | • | DSIRE | Great comprehensive federal, state, and utility incentives. Use filters to narrow search
Simple Payback |  | 0 | years |  |  | • | Washington Incentives | Washington incentives.
[6 empty] | • | Energy Trust | Energy Trust incentives for customers paying a public purpose charge
Incentive Analysis Summary
Description | Incentive | After Incentive | Payback | Notes
|  |  | (yrs) |  |  | Step 2: Order the incentives properly.
[5 empty] | <<HIDE ROW |  | Typically it is safe to order by federal incentives, then state, then finally municipality/local incentives. However, some incentives stipulate when and how they can be applied. Add these special circumstances in the notes. For example the ETO Wind Turbine Incentives says that all incentives for the AR can be 50% of the total project cost. This means that ETO will incentivize anywhere from 0% to 50% of the project or in other words ETO makes up the difference to make total incentives reach 50%.
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
<<HIDE ROW
Totals | 0 | 0 | 0 |  | <<HIDE ROW | Step 3: Fill in incentive values (always use equations rather than hard-code numbers)
Step 4: Review the Notes sections. Hide unnecessary ones, review verbage of ones that apply for accuracy.
No Incentives
This measure does not include the purchase of capital assets and is ineligible for incentives. |  |  |  |  | << Hide or review for accuracy (choose one of three options)
The implementation cost associated with this measure is so small that it does not warrant the time and overhead associated with applying for incentives. Analysts believe this measure already has an attractive simple payback period. |  |  |  |  | Be wary of using the third explanation here. Ask a more experienced analyst for help if you're unable to identify any incentives.
Analysts were unable to identify any published incentives for this measure. This does not necessarily mean incentives are unavailable; custom incentives with utility providers can sometimes be arranged.
REAP |  |  |  |  | << Hide or review for accuracy
You may be eligible for a Rural Energy for America Program grant. These grants are available to agricultural producers who gain 50% or more of their gross income from agricultural operations and small businesses who are located in a rural area as defined by the SBA (Small Business Association). Eligible projects include but are not limited to energy efficiency improvements and renewable energy systems (wind, solar, biomass, geothermal, hydro power and hydrogen-based sources). These grants are awarded on a competitive basis and can be up to 25% of the proposed project's cost, and are limited to $500,000 for renewable energy systems and $250,000 for energy efficiency improvements while the loan guarantee may not exceed $25 million. The combined amount of a grant and loan guarantee may not exceed 75% of the project’s cost.
ETO |  |  |  |  | << Hide or review for accuracy
Energy Trust cash incentives are available to help pay for implementation of energy saving measures deemed cost effective if customers are paying a public purpose charge. Incentives can be anticipated to equal the minimum of 50% of total project cost, $0.25 per kWh saved, or $1 per therm saved.
ESI |  |  |  |  | << Hide or review for accuracy
Bonneville Power Administration's Energy Smart Industrial reimbursement incentive is available to help pay for implementation of energy saving measures that are deemed cost effective and have a minimum 10-year life span. Incentives can be anticipated to equal minimum of 70% of total project cost or $0.25 per kWh saved.
ITC |  |  |  |  | << Hide or review for accuracy
You may also be eligible for a Federal Business Investment Tax Credit. These grants are available to industrial producers and the credit is equal to 27.4% (as of March 1st, 2013 the incentive was reduced from 30% to its current value) of expenditures for solar, fuel cells, small wind turbines, and 10% of expenditures for geothermal systems, microturbines and combined heat and power with no maximum credit. The credits are for eligible systems placed in service on or before December 31, 2016.

## P-T Table
Refrigerant - Pressure/Temperature Table | [7 empty] | Pressure to Temperature Interpolation
Temp | R-11 | R-12 | R-22 | R-123 | R-134a | R-500 | Ammonia |  | Current | Proposed | Input
-20 | - | 0.56 | 10.21 | - | - | 3.22 | 3.58 | Pressure (psig) | 24 | 34
-18 | - | 1.29 | 11.39 | - | - | 4.07 | 4.57 | Refrigerant | Temp (°F) | Temp (°F) | Temp (°F)
-16 | - | 2.04 | 12.61 | - | - | 4.96 | 5.62 | R-11 | 130.0488 | 145.0759 | -
-14 | - | 2.82 | 13.87 | - | 0.36 | 5.87 | 6.71 | R-12 | 24.2027 | 36.6971 | -
-12 | - | 3.64 | 15.18 | - | 1.13 | 6.82 | 7.84 | R-22 | -0.05 | 11.1917 | -
-10 | - | 4.48 | 16.54 | - | 1.94 | 7.81 | 9.02 | R-123 | 135.616 | 150.2119 | -
-8 | - | 5.35 | 17.94 | - | 2.78 | 8.83 | 10.25 | R-134a | 27.3924 | 38.8691 | -
-6 | - | 6.25 | 19.39 | - | 3.66 | 9.88 | 11.54 | R-500 | 15.8808 | 27.8667 | -
-4 | - | 7.18 | 20.89 | - | 4.56 | 10.97 | 12.87 | Ammonia | 10.2222 | 20.4558 | -
-2 | - | 8.14 | 22.44 | - | 5.51 | 12.1 | 14.26
0 | - | 9.13 | 24.04 | - | 6.48 | 13.27 | 15.7
2 | - | 10.16 | 25.69 | - | 7.5 | 14.47 | 17.2
4 | - | 11.22 | 27.4 | - | 8.55 | 15.72 | 18.76
6 | - | 12.32 | 29.16 | - | 9.64 | 17.01 | 20.38
8 | - | 13.45 | 30.97 | - | 10.77 | 18.34 | 22.05
10 | - | 14.62 | 32.85 | - | 11.95 | 19.71 | 23.8
12 | - | 15.82 | 34.78 | - | 13.16 | 21.12 | 25.6
14 | - | 17.06 | 36.77 | - | 14.41 | 22.58 | 27.48
16 | - | 18.34 | 38.82 | - | 15.71 | 24.09 | 29.42
18 | - | 19.66 | 40.94 | - | 17.06 | 25.64 | 31.43
20 | - | 21.02 | 43.11 | - | 18.45 | 27.24 | 33.51
22 | - | 22.41 | 45.35 | - | 19.88 | 28.88 | 35.66
24 | - | 23.85 | 47.65 | - | 21.37 | 30.58 | 37.9
26 | - | 25.33 | 50.03 | - | 22.9 | 32.32 | 40.2
28 | - | 26.86 | 52.46 | - | 24.48 | 34.12 | 42.59
30 | - | 28.42 | 54.97 | - | 26.11 | 35.97 | 45.05
32 | - | 30.04 | 57.55 | - | 27.8 | 37.87 | 47.6
34 | - | 31.69 | 60.2 | - | 29.53 | 39.82 | 50.23
36 | - | 33.39 | 62.92 | - | 31.33 | 41.83 | 52.95
38 | - | 35.14 | 65.71 | - | 33.17 | 43.9 | 55.76
40 | - | 36.94 | 68.58 | - | 35.08 | 46.02 | 58.65
42 | - | 38.78 | 71.53 | - | 37.04 | 48.2 | 61.64
44 | - | 40.68 | 74.55 | - | 39.06 | 50.44 | 64.72
46 | - | 42.62 | 77.65 | - | 41.13 | 52.74 | 67.9
48 | - | 44.62 | 80.83 | - | 43.27 | 55.1 | 71.17
50 | - | 46.66 | 84.09 | - | 45.47 | 57.52 | 74.54
52 | - | 48.76 | 87.4 | - | 47.74 | 60 | 78.02
54 | - | 50.91 | 90.9 | - | 50.07 | 62.55 | 81.59
56 | - | 53.12 | 94.4 | - | 52.46 | 65.16 | 85.28
58 | - | 55.38 | 98 | - | 54.92 | 67.84 | 89.1
60 | - | 57.7 | 101.7 | - | 57.45 | 70.58 | 93
62 | - | 60.07 | 105.5 | - | 60.05 | 73.4 | 97
64 | - | 62.5 | 109.3 | - | 62.72 | 76.28 | 101.1
66 | - | 64.99 | 113.3 | - | 65.46 | 79.23 | 105.3
68 | - | 67.54 | 117.3 | - | 68.27 | 82.25 | 109.7
70 | - | 70.15 | 121.5 | - | 71.16 | 85.3 | 114.2
72 | - | 72.82 | 125.7 | - | 74.12 | 88.5 | 118.8
74 | - | 75.55 | 130.1 | - | 77.16 | 91.7 | 123.5
76 | 0.32 | 78.34 | 134.5 | - | 80.28 | 95.1 | 128.4
78 | 0.92 | 81.2 | 139 | - | 83.47 | 98.5 | 133.4
80 | 1.53 | 84.13 | 143.7 | - | 86.7 | 101.9 | 138.5
82 | 2.16 | 87.1 | 148.4 | - | 90.1 | 105.5 | 143.7
84 | 2.82 | 90.2 | 153.3 | 0.59 | 93.5 | 109.1 | 149.1
86 | 3.49 | 93.3 | 158.2 | 1.21 | 97.1 | 112.8 | 154.6
88 | 4.18 | 96.5 | 163.3 | 1.85 | 100.7 | 116.6 | 160.3
90 | 4.89 | 99.7 | 168.5 | 2.51 | 104.4 | 120.5 | 166.1
92 | 5.62 | 103.1 | 173.7 | 3.19 | 108.2 | 124.4 | 172
94 | 6.37 | 106.5 | 179.1 | 3.9 | 112 | 128.5 | 178.1
96 | 7.14 | 109.9 | 184.6 | 4.62 | 116 | 132.6 | 184.4
98 | 7.94 | 113.5 | 190.3 | 5.36 | 120.1 | 136.8 | 190.8
100 | 8.76 | 117.1 | 196 | 6.13 | 124.2 | 141.1 | 197.3
102 | 9.6 | 120.8 | 201.8 | 6.92 | 128.5 | 145.5 | 204
104 | 10.46 | 124.6 | 207.8 | 7.73 | 132.8 | 150 | 210.9
106 | 11.35 | 128.4 | 213.9 | 8.57 | 137.3 | 154.5 | 217.9
108 | 12.26 | 132.3 | 220.1 | 9.43 | 141.8 | 159.2 | 225.1
110 | 13.19 | 136.3 | 226.4 | 10.31 | 146.5 | 164 | 232.5
112 | 14.15 | 140.4 | 232.9 | 11.22 | 151.2 | 168.8 | 240
114 | 15.13 | 144.6 | 239.5 | 12.15 | 156.1 | 173.8 | 247.7
116 | 16.14 | 148.8 | 246.2 | 13.11 | 161 | 178.8 | 255.5
118 | 17.18 | 153.2 | 253.1 | 14.1 | 166.1 | 183.9 | 263.6
120 | 18.24 | 157.6 | 260 | 15.11 | 171.3 | 189.2 | 271.8
122 | 19.33 | 162.1 | 267.2 | 16.15 | 176.5 | 194.5 | 280.2
124 | 20.45 | 166.7 | 274.4 | 17.22 | 181.9 | 200 | 288.8
126 | 21.59 | 171.3 | 281.8 | 18.32 | 187.5 | 205.5 | 297.6
128 | 22.77 | 176.1 | 289.3 | 19.44 | 193.1 | 211.2 | 306.6
130 | 23.97 | 180.9 | 297 | 20.59 | 198.8 | 217 | 315.7
132 | 25.2 | 185.9 | 304.8 | 21.78 | 204.7 | 222.8 | 325.1
134 | 26.46 | 190.9 | 312.7 | 22.99 | 210.7 | 228.8 | 334.6
136 | 27.75 | 196 | 320.8 | 24.24 | 216.8 | 234.9 | 344.4
138 | 29.07 | 201.2 | 329.1 | 25.51 | 223 | 241.1 | 354.3
140 | 30.42 | 206.5 | 337.5 | 26.82 | 229.4 | 247.4 | 364.5
142 | 31.81 | 211.9 | 346 | 28.16 | 235.8 | 253.8 | 374.9
144 | 33.22 | 217.4 | 354.7 | 29.53 | 242.5 | 260.4 | 385.4
146 | 34.67 | 223 | 363.6 | 30.93 | 249.2 | 267 | 396.2
148 | 36.15 | 228.7 | 372.6 | 32.37 | 256.1 | 273.8 | 407.3
150 | 37.66 | 234.5 | 381.7 | 33.84 | 263.1 | 280.7 | 418.5
152 | 39.21 | 240.4 | 391.1 | 35.35 | 270.2 | 287.7 | 429.9
154 | 40.79 | 246.4 | 400.6 | 36.89 | 277.5 | 294.9 | 441.6
156 | 42.41 | 252.5 | 410.2 | 38.47 | 285 | 302.1 | 453.5
158 | 44.06 | 258.7 | 420.1 | 40.09 | 292.5 | 309.5 | 465.7
160 | 45.75 | 265 | 430.1 | 41.74 | 300.2 | 317.1 | 478
162 | 47.48 | 271.4 | 440.3 | 43.43 | 308.1 | 324.7 | 490.6
164 | 49.24 | 278 | 450.6 | 45.15 | 316.1 | 332.5 | 503.5
166 | 51.04 | 284.6 | 461.1 | 46.92 | 324.3 | 340.4 | 516.6
168 | 52.87 | 291.3 | 471.9 | 48.72 | 332.6 | 348.5 | 529.9
170 | 54.75 | 298.2 | 482.8 | 50.57 | 341.1 | 356.7 | 543.5
172 | 56.66 | 305.2 | 493.9 | 52.45 | 349.7 | 365 | 557.4
174 | 58.61 | 312.2 | 505.1 | 54.37 | 358.5 | 373.5 | 571.5
176 | 60.61 | 319.4 | 516.6 | 56.34 | 367.5 | 382.1 | 585.8
178 | 62.64 | 326.8 | 528.3 | 58.35 | 376.6 | 390.8 | 600.5
180 | 64.71 | 334.2 | 540.2 | 60.4 | 386 | 399.7 | 615.4
182 | 66.83 | 341.7 | 552.3 | 62.49 | 395.4 | 408.8 | 630.5
184 | 68.99 | 349.4 | 564.6 | 64.62 | 405.1 | 418 | 646
186 | 71.19 | 357.2 | 577.1 | 66.81 | 414.9 | 427.4 | 661.7
188 | 73.43 | 365.1 | 589.8 | 69.03 | 425 | 436.9 | 677.7
190 | 75.72 | 373.2 | 602.8 | 71.3 | 435.2 | 446.6 | 693.9
192 | 78.05 | 381.3 | 616 | 73.62 | 445.6 | 456.5 | 710.5
194 | 80.42 | 389.6 | 629.5 | 75.98 | 456.2 | 466.5 | 727.4
196 | 82.84 | 398 | 643.2 | 78.39 | 467 | 476.7 | 744.5
198 | 85.3 | 406.6 | 657.2 | 80.84 | 478.1 | 487.1 | 762
200 | 87.8 | 415.3 | 671.4 | 83.35 | 489.3 | 497.7 | 779.7